## ABOUT
Facility Condition Assessment (FCA) Workbook
Version 1.1
March 2026
#VALUE! | #VALUE! | #VALUE!
This Excel workbook is designed for use by public school districts to collect and analyze data in a Facility Condition Assessment (FCA) process. The tool is made available for users to customize for their one needs.
For detailed instructions on how to use this workbook, view the companion FACILITY CONDITION ASSESSMENT MANUAL at school-infrastructure.org
NOTE: The cost models included in the workbook should be reviewed and updated by the user to reflect current local market conditions.
NOTE: The workbook file is designed to be used for one building. For multiple buildings, simply duplicate the file and maintain a one file per building setup.
ACKNOWLEDGEMENTS AND DISCLAIMERS
Editor: David Sturtz, Sturtz & Company
This Facility Condition Assessment (FCA) Manual outlines guidance for conducting FCAs. The accompanying Excel-based FCA Workbook is a tool to assist school district leaders, facilities staff, and decision-makers in planning, scoping, and managing professionally conducted FCAs. Both are available on the National Center on School Infrastructure (NCSI) website: school-infrastructure.org.
Workbook Provenance and Adaptation
This workbook draws on established FCA practices originally created by the Oregon Department of Education for its Technical Assistance Program (TAP). The materials have been adapted and expanded through the collaborative work of Sturtz & Company, the National Council on School Facilities (NCSF), and the National Center on School Infrastructure (NCSI), building on established state and national FCA frameworks. This manual began as an internal training document and was improved over time through contributions from dedicated professionals. Much gratitude to all who invested their time and expertise.
Important Intended Use Notice
These tools are not a substitute for a comprehensive Facility Condition Assessment conducted by qualified, credentialed professionals. This manual and companion workbook are intended to provide users with 1) education materials pertaining to facility condition assessments, and 2) a Rough Order of Magnitude (ROM) understanding of their building conditions when a professional assessment is not feasible. School districts and other agencies should engage appropriately licensed architects, engineers, and/or certified FCA professionals to perform formal condition assessments, code evaluations, and capital planning analyses whenever possible. LEAs should maintain compliance with state rules and regulations pertaining to the collection or use, directly or indirectly, of facility condition data. If a LEA plans to request capital funds based on this assessment, a certified professional assessor should be employed to perform the assessment or at least review and certify the results.
Technical Limitation
The materials provided do not constitute engineering, architectural, or code compliance services. Users are responsible for obtaining qualified professional evaluations where required by law and/or regulation.
Professional Standards Note
FCAs that inform capital planning, regulatory compliance, or life-safety decisions should follow recognized industry standards (such as ASTM E2018 or comparable state guidance) and be performed under appropriate professional supervision.
Contents of this manual were developed under Award #S184R230005 from the U.S. Department of Education.
However, the contents do not necessarily represent the policy of the Department of Education, and you should not assume endorsement by the Federal Government.
The tool is made available for users to customize for their one needs.
Questions? Feedback?
https://school-infrastructure.org/contact-us/
We would appreciate hearing from you about your experience with this tool. Drop us a line.

## Helpful Information
Helpful Information
1 | Before completing the template it is best to do an informal interview with the individual in charge of the facilities. This is especially helpful when completing the checklists i.e., ADA, Harmful Substances, etc.
2 | Please ensure that you are interviewing the correct person to complete the checklists. For example, you may need to talk to the Internet Service Provider to complete the IT checklist.
3 | It is recommended that you complete the assessment on-site. Enter percentages and levels of action on-site after the walkthrough and before leaving the facility.
4 | In order for the template to accurately calculate information please complete the "Base Information Sheet." Cells highlighted in yellow are required as the rest of the template will not calculated correctly without that information.
5 | In order for the template to function properly do not change information on the READ ONLY tabs (worksheets e.g., "Building Type Budget-READ ONLY")
6 | It is best to use the template in Microsoft Excel as mobile devices and other application platforms such as Apple will not show the comments. However, a "Physical Assessment Comments" tab is located in the template.
7 | Make sure you hover over the upper right hand corner of cells to view comments. They determine the level of action. Pay attention whether a comment says “and” or “or.”
8 | Use “x” to indicate a system is present.
9 | Use “0” or zero to indicate that a system is not present or leave blank.
10 | When entering data in the Percentage of System column (column P), the data must be entered as a percentage of the system. For example, if resilient tile covers 50% of the building and 35% of it needs to be replaced, used 35 in the Percentage of System column. This is true even if the system is a number rather than percentage. For example there are 40 wood doors and 10 need to be replaced, then enter 25 in Percentage of System column (Column P).
11 | When you are using your expertise to override the built-in cost model document that decision in the "Notes" sections. Notes should be added to communicate why you are overriding the template. Example, a system has a key component that needs to be replaced but that replacement is not accurately described in the "Level of Action" comments.
12 | If you have a system not found in the template then add it at the bottom of the "Physical Condition Assessment."
13 | If you know that costs have changed override the cost on the Physical Condition Assessment tab ONLY and note it.
14 | Please note that some units of measure differ from the gross square footage of the building. The new units of measure are provided as comments in the category description. This is to address some of the concerns with using gross square footage for units that aren't really based on square footage. Example: the percentage of exterior doors that are wood is the number of wood exterior doors divided by the total number of exterior doors. If a school has 10 exterior doors and 7 are wood, then 70% of the doors are wood and that is the percentage that goes into the % of Building column.
15 | It is recommended that you create a different assessment Excel workbook for each building.
16 | The default for portables is to list them in the Renovations, Additions, & Prtbls tab. If you require a full assessment of portable classrooms, please create a separate assessment Excel workbook for each building.
17 | If an ADA deficiency is listed in the Physical Condition Assessment tab, then include that in the final costs.
18 | Please remember that this tool is to provide districts with budget level estimates on costs of repairs to buildings. If after reviewing the total costs, including the built in soft cost multiplier, your expert opinion is that the costs are too low, please increase the costs and note it in the "Notes" section.
19 | On the Base Information Sheet, Cell B5: If the campus has more than one building, please specify the building in the Site Name field as well. For example: *Site Name: Rolling Hills Elementary_Main Building *Site Name: Rolling Hills Elementary _Gymnasium
20 | On the HVAC sheet: If there are no HVAC units at the facility, write "No HVAC system at this facility." in cell B12.
21 | On the HVAC sheet: Write "Unavailable" or "N/A" (as appropriate) in all cells that cannot be filled out. If you do not know the "Type", you can leave this cell blank.
22 | Please run a spell check on the Physical Condition Assessment, Dashboard Integration Page, and Roof sheets before submitting the workbook for upload. (Top toolbar àReview à Select "abc Spelling" icon on top left of toolbar)

## Base Information Sheet
Item | Data | Notes / Explanation
District Name: |  | Type District Name
Site Name: |  | Suggested formatting: SITE NAME_BUILDING NAME (the Dashboard site hierarchy is based on what is entered here). To group multiple workbooks at the same site, the SITE NAME must match (i.e., Elementary School - Main & Elementary School - Gym is correct). If one WB says "Elementary School - Main" and another WB says "Elementary - Gym", they would not be grouped together on Dashboard because the left part of the SITE NAMES don't match exactly (Elementary School VS Elementary). If there is only one main building at the site, use the format "Austin Elementary School"; do not add "_Main" at the end of the SITE NAME.
Building Name:
1
Building ID:
Building Type: | Elementary School | Pull-down menu - feeds FCI calculation
Physical Address of Building:
Original Year Built, Years of Additions: |  | List the original building year completed.
Primary Structure Type: |  | What type of construction was used to complete original building
Describe Other Construction Type: |  | If you choose other construction type please describe here
County: |  | Enter County Name
Gross Square Footage: |  | Calculated from exterior face of walls (excluding eaves, outbuilding, porches, canopies, and similar)
Site Acreage: |  | District records
Assessor Company: |  | Name of the company performing the assessment
Initial Assessor Name: |  | For follow up questions
Contact (Phone):
Contact (E-Mail):
Date of Assessment: |  | Use format MM/DD/YYYY
Cost Factor: |  | Insert an estimated local cost inflation factor based on how much local costs are greater/lesser than the base prices in the PCA Cost Tables. (E.g., 1.15 = costs are ~ 15% greater than the average in the PCA Cost Table. If costs are considered average, keep the value "1")
Assigned Inflation Factor: |  | Inflation Assigned for a 30-month period assuming 1 year till bond and 1-1/2 years into a 3-year design/construction cycle (ex: 1.16)
Assigned Soft Development Factor: |  | Assuming design, direct-hire specialists (envelope, commissioning, cost estimating, etc.), state solar, permits, survey, geo, bond issuance, management, furnishings, and 15% contingency (ex: 1.38)
Escalation Beyond 30 months: |  | Inflation Rate Per Annum for Projects (ex: 1.04)
Blue colored box indicates critical data needed for the assessment

## Physical Condition Assessment
District Name: |  | 0 |  |  | FILL OUT ALL INFORMATION ON 'BASE INFORMATION SHEET' BEFORE ENTERING DATA ON THIS SHEET
Site Name: |  | 0 |  |  |  | An unused cell or system that should not receive direct user input | [24 empty] | State Assigned Inflation Factor | 0
Building Name: |  | 0 |  |  |  | An automatically populated cell from user input elsewhere in the file - do not overwrite | [24 empty] | County Cost Factor for Physical Assessment Budget Calculation | 0 | [7 empty] | Update if useful life values are known to be different than the values below. | Based on value in Base Info Sheet, cell B23 or the YR system was renovated. |  | Estimated timeframe and ROM cost within 15 years when a system would require major renovation or replacement.
Today's Date |  | 2026-03-16 |  |  |  | Column / cell needs direct user input (see also column AR to the right to inform Life Cycle Cost Estimates)
Year |  | 1905-07-18
[5 empty] | LEVEL OF NEEDED ACTION | [33 empty] | Manually edit for each assessment
Level 1 | Level 2 | Level 3 | Type (as applicable) | % of Building or Number | None |  | Minor |  | Moderate |  | Major |  | Replace as part of Renovation |  | Replace as singular scope | % of System or Finish | Automated Budget Estimate | Notes | Lookup Key <HIDE> | System Category | [5 empty] | Unit | Major | Replace | Minor | Moderate | MAJOR $ - PCA | REPLACE $ PCA | SF - Major | SF - Replace | Unit - Major | Unit - Replace | System Replacement Value | System CI | Year system received major reno or replacement | Estimated useful life | System age | Estimate year of end of useful life | Yr 0 LC $ | Yrs 1-5 LC $ | Yrs 6-10 LC $ | YRs 11-15 LC $
A SUBSTRUCTURE
A10 Foundations
A SUBSTRUCTURE | A10 Foundations | A1010 Standard Foundations |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | A1010 Standard Foundations_blank | Foundation | [5 empty] | SF | X |  | 0.6549 | 13.098 | 36.2553 | 0 | 0 | - | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
A SUBSTRUCTURE | A10 Foundations | A1020 Special Foundations |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | A1020 Special Foundations_blank | Foundation | [5 empty] | SF | X |  | 0.6549 | 19.647 | 46.2097 | 0 | 0 | - | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
A SUBSTRUCTURE | A10 Foundations | A1030 Slab on Grade |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | A1030 Slab on Grade_blank | Foundation | [5 empty] | SF | X |  | 2.7899 | 12.4431 | 34.7097 | 0 | 0 | - | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
A SUBSTRUCTURE | A10 Foundations
A SUBSTRUCTURE | A10 Foundations | A2010 Basement Excavation | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace
A SUBSTRUCTURE | A10 Foundations | A2020 Basement Walls |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | A2020 Basement Walls_blank | Foundation | [5 empty] | SF | X |  | 0.87757 | 2.7899 | 11.7358 | 0 | 0 | - | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL
| B10 Superstructure | A2020 Basement Walls
B SHELL | B10 Superstructure | B1010 Floor Construction | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B1010 Floor Construction_Wood | Interior Structure | [5 empty] | SF |  | X | 5.3625 | 12.012 | 76.8625 | 201.9875 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
B SHELL | B10 Superstructure | B1010 Floor Construction | Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B1010 Floor Construction_Steel | Interior Structure | [5 empty] | SF |  | X | 7.7935 | 15.3153 | 81.3241 | 202.4451 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B10 Superstructure | B1010 Floor Construction | Concrete |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B1010 Floor Construction_Concrete | Interior Structure | [5 empty] | SF |  | X | 9.1686 | 18.3372 | 69.4194 | 161.1054 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B10 Superstructure | B1020 Roof Construction | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B1020 Roof Construction_Wood | Roofing | [5 empty] | SF |  | X | 5.8094 | 13.6207 | 58.9875 | 157.3 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B10 Superstructure | B1020 Roof Construction | Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B1020 Roof Construction_Steel | Roofing | [5 empty] | SF |  | X | 8.4549 | 16.8204 | 66.1375 | 164.45 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B10 Superstructure | B1020 Roof Construction | Concrete |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B1020 Roof Construction_Concrete | Roofing | [5 empty] | SF |  | X | 9.8497 | 20.5377 | 56.3214 | 129.6702 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
B20 Exterior Enclosure
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Concrete Formed / Tilt |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2010 Exterior Walls_Concrete Formed / Tilt | Exterior Structure | [5 empty] | SF | x |  | 4.2569 | 6.1561 | 26.196 | 0 | 0 | - | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Masonry |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2010 Exterior Walls_Masonry | Exterior Structure | [5 empty] | SF |  | X | 4.2569 | 8.8019 | 27.663 | 42.8698 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/ Wood Siding |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2010 Exterior Walls_Framed w/ Wood Siding | Exterior Structure | [5 empty] | SF |  | X | 5.4876 | 10.4032 | 33.0688 | 45.5991 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Metal Panel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2010 Exterior Walls_Framed w/Metal Panel | Exterior Structure | [5 empty] | SF |  | X | 6.3814 | 12.1907 | 34.32 | 54.5366 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Stucco |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2010 Exterior Walls_Framed w/Stucco | Exterior Structure | [5 empty] | SF |  | X | 4.0211 | 7.623 | 26.196 | 40.1978 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Masonry Veneer |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2010 Exterior Walls_Framed w/Masonry Veneer | Exterior Structure | Window Unit Calculator in feet |  |  |  |  | SF |  | X | 3.2221 | 5.8679 | 32.0901 | 50.5714 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 100 | 2026 | 100 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2020 Exterior Windows_Wood | Exterior/Interior Windows | Total Sq. ft. |  | Number of Units |  |  | Unit |  | X | 89.375 | 357.5 | 893.75 | 1787.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Aluminum/Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2020 Exterior Windows_Aluminum/Steel | Exterior/Interior Windows |  |  | 0 |  |  | Unit |  | X | 31.5 | 126 | 1102.5 | 2205 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Clad |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2020 Exterior Windows_Clad | Exterior/Interior Windows | [5 empty] | Unit |  | X | 119.07 | 476.28 | 1587.6 | 3175.2 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Curtain Wall |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2020 Exterior Windows_Curtain Wall | Exterior/Interior Windows | Window Unit Calculator in inches |  |  |  |  | Unit |  | X | 39.69 | 158.76 | 1190.7 | 2381.4 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2030 Exterior Doors_Wood | Doors | Total Sq. in. |  | Number of Units |  |  | Unit |  | X | 446.875 | 1787.5 | 2681.25 | 3575 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Hollow Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B2030 Exterior Doors_Hollow Metal | Doors |  |  | 0 |  |  | Unit |  | X | 446.875 | 1787.5 | 2323.75 | 3217.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Storefront |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B2030 Exterior Doors_Storefront | Doors | [5 empty] | Unit |  | X | 450.45 | 2162.16 | 4324.32 | 5405.4 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Overhead Metal Garage |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B2030 Exterior Doors_Overhead Metal Garage | Doors | [5 empty] | Unit |  | X | 268.125 | 536.25 | 1072.5 | 2681.25 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Rollup Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B2030 Exterior Doors_Rollup Metal | Doors | [5 empty] | Unit |  | X | 178.75 | 446.875 | 893.75 | 1787.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B30 Roofing
B SHELL | B30 Roofing | B3010 Roof Coverings | Asphalt Shingle |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B3010 Roof Coverings_Asphalt Shingle | Roofing | [5 empty] | SF |  | X | 2.3058 | 6.5075 | 18.361 | 25.62 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Modified Bitumen |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B3010 Roof Coverings_Modified Bitumen | Roofing | [5 empty] | SF |  | X | 2.3058 | 6.5075 | 18.361 | 25.62 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Gravel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B3010 Roof Coverings_Gravel | Roofing | [5 empty] | SF |  | X | 2.6816 | 6.7978 | 20.0861 | 44.408 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Spanish Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B3010 Roof Coverings_Spanish Tile | Roofing | [5 empty] | SF |  | X | 3.885 | 9.1375 | 25.2525 | 52.836 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Built-Up |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | B3010 Roof Coverings_Built-Up | Roofing | [5 empty] | SF |  | X | 2.6816 | 6.7978 | 20.0861 | 44.408 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Single Ply |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B3010 Roof Coverings_Single Ply | Roofing | [5 empty] | SF |  | X | 4.0138 | 7.2761 | 19.3175 | 40.992 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B3010 Roof Coverings_Metal | Roofing | [5 empty] | SF |  | X | 4.29 | 9.6167 | 25.025 | 57.2 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Concrete Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B3010 Roof Coverings_Concrete Tile | Roofing | [5 empty] | SF |  | X | 3.885 | 9.1375 | 25.2525 | 52.836 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3020 Roof Openings | Skylights |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B3020 Roof Openings_Skylights | Roofing | [5 empty] | SF |  | X | 0.13986 | 0.41958 | 1.3986 | 2.7972 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
B SHELL | B30 Roofing | B3020 Roof Openings | Access Hatch |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | B3020 Roof Openings_Access Hatch | Roofing | [5 empty] | Unit |  | X | 368.75 | 737.5 | 2212.5 | 5162.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C INTERIORS
C10 Interior Construction
C INTERIORS | C10 Interior Construction | C1010 Partitions | Framed |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C1010 Partitions_Framed | Interior Structure | [5 empty] | SF |  | X | 3.9683 | 11.9048 | 19.8413 | 24.8889 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1010 Partitions | Masonry |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C1010 Partitions_Masonry | Interior Structure | [5 empty] | SF |  | X | 6.811 | 12.4431 | 23.9038 | 38.22 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1010 Partitions | Curtain Wall |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C1010 Partitions_Curtain Wall | Interior Structure | [5 empty] | SF |  | X | 3.843 | 15.372 | 76.86 | 384.3 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C1020 Interior Doors_Wood | Doors | [5 empty] | Unit |  | X | 446.875 | 1430 | 2323.75 | 3217.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Hollow Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C1020 Interior Doors_Hollow Metal | Doors | [5 empty] | Unit |  | X | 446.875 | 1430 | 1966.25 | 2860 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Storefront |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C1020 Interior Doors_Storefront | Doors | [5 empty] | Unit |  | X | 450.45 | 2162.16 | 4324.32 | 5405.4 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Overhead Metal Garage |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C1020 Interior Doors_Overhead Metal Garage | Doors | [5 empty] | Unit |  | X | 268.125 | 536.25 | 1072.5 | 2681.25 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Rollup Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C1020 Interior Doors_Rollup Metal | Doors | [5 empty] | Unit |  | X | 178.75 | 446.875 | 893.75 | 1787.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | Interior Windows | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | Interior Windows_Wood | Exterior/Interior Windows | Window Unit Calculator in feet |  |  |  |  | Unit |  | X | 89.375 | 357.5 | 893.75 | 1787.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | Interior Windows | Aluminum/Steel |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | Interior Windows_Aluminum/Steel | Exterior/Interior Windows | Total Sq. ft. |  | Number of Units |  |  | Unit |  | X | 31.5 | 126 | 1102.5 | 2205 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C INTERIORS | C10 Interior Construction | Interior Windows | Clad |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | Interior Windows_Clad | Exterior/Interior Windows |  |  | 0 |  |  | Unit |  | X | 115.29 | 461.16 | 1537.2 | 3074.4 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
| C20 Stairs | [13 empty] | Replace
C INTERIORS | C20 Stairs | C2010 Stair Construction | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C2010 Stair Construction_Wood | Interior Structure | Window Unit Calculator in inches |  |  |  |  | Unit |  | X | 893.75 | 8937.5 | 19662.5 | 44687.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 15 | 2026 | 15 | 0 | 0 | 0 | 0
C INTERIORS | C20 Stairs | C2010 Stair Construction | Metal |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C2010 Stair Construction_Metal | Interior Structure | Total Sq. in. |  | Number of Units |  |  | Unit |  | X | 1340.625 | 8937.5 | 26812.5 | 53625 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 15 | 2026 | 15 | 0 | 0 | 0 | 0
C INTERIORS | C20 Stairs | C2010 Stair Construction | Concrete |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C2010 Stair Construction_Concrete | Interior Structure |  |  | 0 |  |  | Unit |  | X | 885 | 8850 | 23600 | 41300 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 15 | 2026 | 15 | 0 | 0 | 0 | 0
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Concrete Fill |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C2020 Stair Finishes_Concrete Fill | Interior Structure | [5 empty] | Unit |  | X | 982.35 | 1964.7 | 3929.4 | 6549 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Resilient |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C2020 Stair Finishes_Resilient | Interior Structure | [5 empty] | Unit |  | X | 654.9 | 982.35 | 1964.7 | 3274.5 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Wood |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C2020 Stair Finishes_Wood | Interior Structure | [5 empty] | Unit |  | X | 793.65 | 1587.3 | 2380.95 | 3968.25 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Metal Grating |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C2020 Stair Finishes_Metal Grating | Interior Structure | [5 empty] | Unit |  | X | 952.38 | 1904.76 | 3174.6 | 4761.9 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
C30 Interior Finishes
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Paint on Masonry |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3010 Wall Finishes_Paint on Masonry | Interior Structure | [5 empty] | SF |  | X | 2.934 | 4.1914 | 5.1082 | 5.7238 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wallboard |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3010 Wall Finishes_Wallboard | Interior Structure | [5 empty] | SF |  | X | 2.6458 | 3.2221 | 6.8765 | 10.557 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wainscot |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3010 Wall Finishes_Wainscot | Interior Structure | [5 empty] | SF |  | X | 2.6458 | 3.5365 | 7.0729 | 11.1333 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wood Paneling |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3010 Wall Finishes_Wood Paneling | Interior Structure | [5 empty] | SF |  | X | 3.2063 | 11.9048 | 15.873 | 23.8095 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Vinyl Paneling |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C3010 Wall Finishes_Vinyl Paneling | Interior Structure | [5 empty] | SF |  | X | 2.6458 | 9.627 | 12.7706 | 15.7176 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Formica |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C3010 Wall Finishes_Formica | Interior Structure | [5 empty] | SF |  | X | 3.4965 | 10.8392 | 13.986 | 20.979 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Ceramic Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C3010 Wall Finishes_Ceramic Tile | Interior Structure | [5 empty] | SF |  | X | 1.1788 | 1.5718 | 2.6196 | 3.1828 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Carpet / Soft Surface |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Carpet / Soft Surface | Flooring | [5 empty] | SF |  | X | 0.39294 | 5.2392 | 8.7495 | 11.3691 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Resilient Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Resilient Tile | Flooring | [5 empty] | SF |  | X | 1.3229 | 2.947 | 6.2346 | 8.9066 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Resilient Sheet |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Resilient Sheet | Flooring | [5 empty] | SF |  | X | 2.6458 | 7.8588 | 15.7176 | 18.3372 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Polished Concrete |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Polished Concrete | Flooring | [5 empty] | SF |  | X | 2.6458 | 6.2216 | 11.7882 | 14.4078 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Ceramic Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Ceramic Tile | Flooring | [5 empty] | SF |  | X | 4.9903 | 15.7176 | 32.9284 | 35.548 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Liquid Applied |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Liquid Applied | Flooring | [5 empty] | SF |  | X | 5.2392 | 10.3343 | 18.4813 | 21.1009 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Wood Sports Floor |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3020 Floor Finishes_Wood Sports Floor | Flooring | [5 empty] | SF |  | X | 8.9375 | 12.5125 | 32.175 | 35.75 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 40 | 2026 | 40 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Wallboard |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3030 Ceiling Finishes_Wallboard | Interior Structure | [5 empty] | SF |  | X | 4.1128 | 9.1686 | 11.7882 | 15.7176 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Lay-In Ceiling Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3030 Ceiling Finishes_Lay-In Ceiling Tile | Interior Structure | [5 empty] | SF |  | X | 1.3098 | 1.8206 | 5.2392 | 10.4784 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Glued-Up Ceiling Tile |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3030 Ceiling Finishes_Glued-Up Ceiling Tile | Interior Structure | [5 empty] | SF |  | X | 0.85137 | 1.3098 | 3.2745 | 6.2085 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Tectum |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | C3030 Ceiling Finishes_Tectum | Interior Structure | [5 empty] | SF |  | X | 0.85137 | 1.3098 | 3.2745 | 6.2085 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Painted Structure |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | C3030 Ceiling Finishes_Painted Structure | Interior Structure | [5 empty] | SF |  | X | 0.52392 | 0.98235 | 2.6196 | 4.2045 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
D SERVICES
D10 Conveying
D SERVICES | D10 Conveying | D1010 Elevators & Lifts |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D1010 Elevators & Lifts_blank | Interior Structure | [5 empty] | Unit |  | X | 7789.272 | 12520.704 | 23476.32 | 84514.752 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
D SERVICES | D10 Conveying | D1020 Escalators & Moving Walks |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D1020 Escalators & Moving Walks_blank | Interior Structure | [5 empty] | Unit |  | X | 5322.45 | 15835.008 | 156692.928 | 172137.76 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D10 Conveying | D1090 Other Conveying Systems |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D1090 Other Conveying Systems_blank | Interior Structure | [5 empty] | Unit |  | X | 1520.7 | 6260.352 | 38017.5 | 41100 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
D20 Plumbing
D SERVICES | D20 Plumbing | D2010 Plumbing Fixtures |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D2010 Plumbing Fixtures_blank | Plumbing | [5 empty] | Unit |  | X | 130.98 | 654.9 | 1964.7 | 3929.4 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 15 | 2026 | 15 | 0 | 0 | 0 | 0
D SERVICES | D20 Plumbing | D2020 Domestic Water Distribution |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | D2020 Domestic Water Distribution_blank | Plumbing | [5 empty] | SF |  | X | 1.6111 | 2.2005 | 9.5353 | 15.7176 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D20 Plumbing | D2030 Sanitary Waste |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D2030 Sanitary Waste_blank | Plumbing | [5 empty] | SF |  | X | 0.6549 | 2.0564 | 2.4231 | 2.7113 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D20 Plumbing | D2040 Rain Water Drainage |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D2040 Rain Water Drainage_blank | Plumbing | [5 empty] | SF |  | X | 0.39294 | 1.3229 | 2.4231 | 3.078 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
D SERVICES | [5 empty] | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace | [10 empty] | SF |  | X | 0 | 0 | 0 | 0 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
| D30 HVAC | [19 empty] | HVAC
D SERVICES | D30 HVAC | D3010 Energy Supply |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3010 Energy Supply_blank | HVAC | Age | # of units | Tons | Cost | % of Total Tons | SF |  | X | 1.8978 | 4.2275 | 11.186 | 19.6565 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 19 | 2026 | 19 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Boiler |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3020 Heat Generating Systems_Boiler | HVAC | 10-14 years old | 0 | 0 | 0 | #DIV/0! | SF |  | X | 3.3974 | 4.3393 | 8.6618 | 16.0117 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Air Handler |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3020 Heat Generating Systems_Air Handler | HVAC | 15+ years old | 0 | 0 | 0 | #DIV/0! | SF |  | X | 1.2614 | 3.1956 | 4.0534 | 9.7887 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Furnace |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3020 Heat Generating Systems_Furnace | HVAC |  | Total Replacement Cost |  | 0 |  | SF |  | X | 1.2446 | 2.2537 | 4.1375 | 7.1649 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Heat Exchanger |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3020 Heat Generating Systems_Heat Exchanger | HVAC | [5 empty] | SF |  | X | 0.33638 | 0.94186 | 1.6987 | 3.3974 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3030 Cooling Generating Systems | Component of air handler |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3030 Cooling Generating Systems_Component of air handler | HVAC | [5 empty] | SF |  | X | 0.84095 | 2.0687 | 4.0534 | 6.4921 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3030 Cooling Generating Systems | Stand alone chiller |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3030 Cooling Generating Systems_Stand alone chiller | HVAC | [5 empty] | SF |  | X | 1.2614 | 3.1956 | 4.0534 | 9.3177 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3040 Distribution Systems | Ductwork |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3040 Distribution Systems_Ductwork | HVAC | [5 empty] | SF |  | X | 0.84095 | 3.0106 | 3.5824 | 8.6618 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3040 Distribution Systems | Hot water return & supply |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3040 Distribution Systems_Hot water return & supply | HVAC | [5 empty] | SF |  | X | 2.0687 | 2.8256 | 7.5686 | 14.4139 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3050 Terminal & Package Units | Above ceiling VAV unit |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3050 Terminal & Package Units_Above ceiling VAV unit | HVAC | [5 empty] | SF |  | X | 2.0687 | 4.0534 | 6.7781 | 13.0347 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3050 Terminal & Package Units | In-room ventilator unit |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3050 Terminal & Package Units_In-room ventilator unit | HVAC | [5 empty] | SF |  | X | 3.3638 | 9.0486 | 20.1828 | 26.8431 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3050 Terminal & Package Units | In-room radiant unit |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3050 Terminal & Package Units_In-room radiant unit | HVAC | [5 empty] | SF |  | X | 0.84095 | 1.8837 | 4.0534 | 5.2812 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3060 Controls & Instrumentation |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3060 Controls & Instrumentation_blank | HVAC | [5 empty] | SF |  | X | 0.94186 | 1.5137 | 4.5243 | 8.6113 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3070 Systems Testing & Balancing |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D3070 Systems Testing & Balancing_blank | HVAC | [5 empty] | SF |  | X | 0 | 0 | 0 | 2.0846 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
D SERVICES | D30 HVAC | D3090 Other HVAC Systems & Equipment | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace
D40 Fire Protection
D SERVICES | D40 Fire Protection | D4010 Sprinklers |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D4010 Sprinklers_blank | Safety/Security | [5 empty] | SF |  | X | 1.5583 | 5.6162 | 14.2718 | 28.7597 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 24 | 2026 | 24 | 0 | 0 | 0 | 0
D SERVICES | D40 Fire Protection | D4020 Standpipes |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D4020 Standpipes_blank | Safety/Security | [5 empty] | SF |  | X | 2.1292 | 3.4561 | 8.8717 | 15.7993 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
D SERVICES | D40 Fire Protection | D4030 Fire Protection Specialties |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D4030 Fire Protection Specialties_blank | Safety/Security | [5 empty] | SF |  | X | 11.5393 | 11.5393 | 43.4199 | 63.0669 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
D SERVICES | D40 Fire Protection | D4090 Other Fire Protection Systems | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace | [10 empty] | SF |  | X | 0 | 0 | 0 | 0 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 25 | 65 | 1983 | 0 | 0 | 0 | 0
D50 Electrical
D SERVICES | D50 Electrical | D5010 Electrical Service & Distribution |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5010 Electrical Service & Distribution_blank | Electrical | [5 empty] | SF |  | X | 1.9119 | 5.5648 | 9.7461 | 12.6062 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 11 | 2026 | 11 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5020 Lighting and Branch Wiring |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5020 Lighting and Branch Wiring_blank | Electrical | [5 empty] | SF |  | X | 1.9119 | 6.2176 | 8.5337 | 27.9792 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Voice / Data System |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Voice / Data System | Electrical | [5 empty] | SF |  | X | 0.31088 | 1.9119 | 5.658 | 18.6528 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Clock / Intercom System |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Clock / Intercom System | Electrical | [5 empty] | SF |  | X | 0.15544 | 0.43523 | 1.5544 | 3.1088 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Closed Circuit Surveillance |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Closed Circuit Surveillance | Electrical | [5 empty] | SF |  | X | 0.15544 | 0.5285 | 1.9119 | 3.4663 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Access Control System |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Access Control System | Electrical | [5 empty] | SF |  | X | 0.10881 | 0.3886 | 1.5544 | 3.1088 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Intrusion Alarm System |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Intrusion Alarm System | Electrical | [5 empty] | SF |  | X | 0.10881 | 0.2487 | 1.1347 | 2.3316 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Fire Alarm / Detection |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Fire Alarm / Detection | Safety/Security | [5 empty] | SF |  | X | 0.34197 | 0.73057 | 3.3109 | 6.6062 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Lighting Control System |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | D5030 Communications & Security_Lighting Control System | Electrical | [5 empty] | SF |  | X | 0.17098 | 0.3886 | 1.3057 | 2.487 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 2026 | 12 | 0 | 0 | 0 | 0
D SERVICES | D50 Electrical | D5090 Other Electrical Systems | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace | [10 empty] | SF |  | X | 0 | 0 | 0 | 0 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 12 | 65 | 1970 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS
E10 Equipment
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1010 Commercial Equipment | Food Service |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E1010 Commercial Equipment_Food Service | Furnishing, Fixtures, Equipment | [5 empty] | SF |  | X | 0.69948 | 1.1347 | 1.399 | 3.6528 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1010 Commercial Equipment | Vocational |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E1010 Commercial Equipment_Vocational | Furnishing, Fixtures, Equipment | [5 empty] | SF |  | X | 2.1712 | 5.5106 | 10.8914 | 39.1878 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Science |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E1020 Institutional Equipment_Science | Furnishing, Fixtures, Equipment | [5 empty] | Unit |  | X | 2.5938 | 6.5847 | 13.0143 | 46.8261 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Art |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E1020 Institutional Equipment_Art | Furnishing, Fixtures, Equipment | [5 empty] | Unit |  | X | 2.3343 | 3.6934 | 7.375 | 32.45 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Stage Performance |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E1020 Institutional Equipment_Stage Performance | Furnishing, Fixtures, Equipment | [5 empty] | Unit |  | X | 7.434 | 17.8416 | 37.17 | 89.208 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Restroom Accessories/Stalls |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace |  |  | 0 |  | E1020 Institutional Equipment_Restroom Accessories/Stalls | Furnishing, Fixtures, Equipment | [5 empty] | SF |  | X | 0.28816 | 1.6634 | 0.51082 | 2.5934 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS |  | E1030 Vehicular Equipment | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace
E EQUIPMENT & FURNISHINGS |  | E1090 Other Equipment | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace
E20 Furnishings
E EQUIPMENT & FURNISHINGS | E20 Furnishings | E2010 Fixed Furnishings |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E2010 Fixed Furnishings_blank | Furnishing, Fixtures, Equipment | [5 empty] | SF |  | X | 2.0502 | 3.4662 | 5.5165 | 13.747 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 75 | 2026 | 75 | 0 | 0 | 0 | 0
E EQUIPMENT & FURNISHINGS | E20 Furnishings | E2020 Movable Furnishings |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | E2020 Movable Furnishings_blank | Furnishing, Fixtures, Equipment | [5 empty] | SF |  | X | 13.098 | 0 | 0 | 31.4352 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 50 | 2026 | 50 | 0 | 0 | 0 | 0
F SPECIAL CONSTRUCTION & DEMOLITION - NOT USED
G BUILDING SITE WORK
| G10 Site Preparation | E2020 Movable Furnishings | NOT USED
G20 Site Improvements
G BUILDING SITE WORK | G20 Site Improvements | G2010 Roadways |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G2010 Roadways_blank | Parking/Traffic | [5 empty] | Unit |  | X | 2.0564 | 5.2392 | 8.5137 | 10.4784 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 20 | 2026 | 20 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G20 Site Improvements | G2020 Parking Lots |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G2020 Parking Lots_blank | Parking/Traffic | [5 empty] | Unit |  | X | 2.0564 | 5.2392 | 8.5137 | 10.4784 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 21 | 2026 | 21 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G20 Site Improvements | G2030 Pedestrian Paving |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G2030 Pedestrian Paving_blank | Parking/Traffic | [5 empty] | Unit |  | X | 2.6196 | 5.8941 | 11.7882 | 14.4078 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 22 | 2026 | 22 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G20 Site Improvements | G2040 Site Development |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G2040 Site Development_blank | Site | [5 empty] | Unit |  | X | 7.8588 | 10.4784 | 32.745 | 45.843 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 23 | 2026 | 23 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G20 Site Improvements | G2050 Landscaping |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G2050 Landscaping_blank | Site | [5 empty] | Unit |  | X | 2.6196 | 2.8816 | 3.0125 | 3.2745 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 24 | 2026 | 24 | 0 | 0 | 0 | 0
G30 Site Mechanical Utilities
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3010 Water Supply | Domestic |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3010 Water Supply_Domestic | Plumbing | [5 empty] | Unit |  | X | 0 | 0 | 0 | 92.807 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 24 | 2026 | 24 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3010 Water Supply | Fire |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3010 Water Supply_Fire | Plumbing | [5 empty] | Unit |  | X | 0 | 0 | 0 | 92.807 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 25 | 2026 | 25 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3020 Sanitary Sewer |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3020 Sanitary Sewer_blank | Plumbing | [5 empty] | Unit |  | X | 0 | 0 | 0 | 64.251 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 26 | 2026 | 26 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3030 Storm Sewer |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3030 Storm Sewer_blank | Plumbing | [5 empty] | Unit |  | X | 2.95 | 4.425 | 5.9 | 10.325 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 27 | 2026 | 27 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3040 Heating Distribution |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3040 Heating Distribution_blank | Plumbing | [5 empty] | Unit |  | X | 0 | 0 | 0 | 437.294 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 28 | 2026 | 28 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3050 Cooling Distribution |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3050 Cooling Distribution_blank | Plumbing | [5 empty] | Unit |  | X | 0 | 0 | 0 | 630.7125 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 29 | 2026 | 29 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3060 Fuel Distribution |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G3060 Fuel Distribution_blank | Plumbing | [5 empty] | Unit |  | X | 0 | 0 | 0 | 78.529 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 30 | 2026 | 30 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3090 Other Site Mechanical Utilities | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace | [10 empty] | Unit |  | X | 0 | 0 | 0 | 0 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 31 | 65 | 2008 | 0 | 0 | 0 | 0
| G40 Site Electrical Utilities | G3090 Other Site Mechanical Utilities
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4010 Electrical Distribution | Service |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G4010 Electrical Distribution_Service | Electrical | [5 empty] | SF |  | X | 0 | 0 | 1.2998 | 3.9932 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 31 | 2026 | 31 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4010 Electrical Distribution | Generator |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G4010 Electrical Distribution_Generator | Electrical | [5 empty] | Unit |  | X | 2737.6 | 13688 | 88972 | 123192 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 32 | 2026 | 32 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4020 Site Lighting |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G4020 Site Lighting_blank | Electrical | [5 empty] | Unit |  | X | 5129.52 | 0 | 0 | 8704.64 | FALSE | FALSE | - | 0 | 0 | #DIV/0! |  | 33 | 2026 | 33 | 0 | 0 | 0 | 0
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4030 Site Communications & Security |  |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace |  | 0 |  | G4030 Site Communications & Security_blank | Electrical | [5 empty] | SF |  | X | 0 | 0 | 0 | 18.6528 | - | 0 | FALSE | FALSE | 0 | #DIV/0! |  | 34 | 2026 | 34 | 0 | 0 | 0 | 0
|  | G4090 Other Site Electrical Utilities | NOT USED |  |  | None |  | Minor |  | Moderate |  | Major |  | Replace | Replace
| G90 Other Site Construction | G4090 Other Site Electrical Utilities | NOT USED
OTHER
| Description of System | [8 empty] | Unit of Measure |  | Quantity |  | Unit Budget | Unit Budget |  | Extended | Notes
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
0
[11 empty] | Physical Condition Budget Sub-Total | [5 empty] | 0
[11 empty] | Budgeted Development Costs | [5 empty] | 0
[11 empty] | Physical Condition Budget TOTAL | [5 empty] | 0
[11 empty] | Cost with Escalation to 2023 | [5 empty] | 0
[11 empty] | Cost with Escalation to 2024 | [5 empty] | 0
[11 empty] | Cost with Escalation to 2025 | [5 empty] | 0
[11 empty] | Replacement Budget | [5 empty] | 0
[11 empty] | Facility Condition Index (FCI) | [5 empty] | #DIV/0!
SAFETY & SECURITY IMPROVEMENTS
If there are no S&S recommendations, write "None at this time."
PORTABLE CLASSROOMS
|  | Portable Number |  | Age of Portable |  | Square Footage |  | Notes | [10 empty] | Date Placed on Site
|  | none |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | 0 |  | 0 |  | 0 |  | 0 | [10 empty] | 0
|  | Occupancy |  | Year Built |  | Area | [12 empty] | Total Value
|  | TOTAL: | [16 empty] | 0
Note on C10: Standard spread and strip/perimeter footings. Based on building's gross square footage.
Note on H10: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on J10: Larger separation cracks occurring and/or evidence of shrinking heaving in areas
Note on L10: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C11: Pilings or other extended foundation systems that overcome non-standard soil conditions. Based on building's gross square footage.
Note on H11: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on J11: Larger separation cracks occurring and/or evidence of shrinking heaving in areas
Note on L11: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C12: Standard ground-set concrete slab. If slab is elevated, i.e. has a crawl space or basement, apply conditions to B1010 instead. Based on building's gross square footage.
Note on H12: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on J12: Larger separation cracks occurring and/or evidence of shrinking heaving in areas
Note on L12: Differential settlement occurring - requires removal of section of slab, adjustment to sub-grade, and new infill
Note on C15: Assumed as concrete walls with water-proofing on the exterior. Includes only the structural portion and not the wall finishes. Based on building's gross square footage.
Note on H15: Inadequate below grade venting is observed - cut in and add venting.
Note on J15: Wall is cracked and spalling requiring route and fill and patch and re-finish.
Note on L15: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied.
Note on C18: A suspended floor including the structural members and floor construction, but not including the actual finish.
Note on H18: Minor issue observed requiring maintenance or repair. Does not require removal of deck.
Note on J18: Deck lifting or uneven not the structural support below - requires repair of the deck.
Note on L18: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on N18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on P18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on H19: Minor issue observed requiring maintenance or repair. Does not require removal of deck.
Note on J19: Deck lifting or uneven not the structural support below - requires repair of the deck.
Note on L19: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on N19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on P19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on H20: Minor issue observed requiring maintenance or repair. Does not require removal of deck.
Note on J20: Deck lifting or uneven not the structural support below - requires repair of the deck.
Note on L20: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck.
Note on N20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement.
Note on P20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on C21: The roof structure referring to the supporting structure and the deck but excluding the roofing itself.
Note on H21: Minor issue observed requiring maintenance or repair. Does not require removal of deck.
Note on J21: Roof decking is separating from roof system requiring repair not replacement
Note on L21: Evidence of a spongy decking from water intrusion - replacing the deck but not the trusses.
Note on N21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on P21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on H22: Minor issue observed requiring maintenance or repair. Does not require removal of deck.
Note on J22: Roof decking is separating from roof system requiring repair not replacement
Note on L22: Evidence of a flexing decking from water intrusion/rust - replacing the deck but not the trusses.
Note on N22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on P22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on H23: Minor issue observed requiring maintenance or repair. Does not require removal of deck.
Note on J23: Roof decking is separating from roof system requiring repair not replacement
Note on L23: Evidence of a spongy/spalling deck from water intrusion - replacing the deck but not the beams.
Note on N23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement.
Note on P23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on H25: Surface is intact but finish is deteriorated - paint.
Note on J25: Cracks visible - route and patch prior to painting.
Note on L25: Major cracks visible - panel may need major repair or replacement
Note on H26: Surface is in tact but finish is deteriorated - paint.
Note on J26: Some blocks are damaged, needing patch and repair prior to sealing or painting.
Note on L26: Sections are damaged, needing major repair or replacement prior to sealing or painting.
Note on N26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on P26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on H27: Surface is in tact but finish is deteriorated - paint.
Note on J27: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on L27: A number of panels are damaged, requiring major repair prior to re-painting.
Note on N27: The panels are lifting or separating or otherwise losing their integrity - remove and replace.
Note on P27: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on H28: Surface is in tact but finish is deteriorated - paint.
Note on J28: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on L28: A number of panels are damaged, requiring major repair prior to re-painting.
Note on N28: The panels are lifting or separating or otherwise losing their integrity - remove and replace.
Note on P28: System in failure with evidence of water intrusion - remove and replace
Note on H29: Surface is in tact but finish is deteriorated - paint.
Note on J29: Cracks visible - route and patch prior to painting.
Note on L29: Large Cracks visible - route repair, fill, patch prior to painting.
Note on N29: System in failure with evidence of water intrusion - remove and replace.
Note on P29: Masonry visibly damaged and requiring removal and replacement
Note on H30: Minor repairs needed to mortar, prep, and re-sealing.
Note on J30: Mortar missing in a majority of areas requiring complete re-pointing and sealing.
Note on L30: Mortar missing in a majority of areas causing structural damage requiring complete re-pointing and sealing.
Note on N30: Masonry visibly damaged and requiring removal and replacement.
Note on P30: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D31: Enter # of wood windows. 1 window = a standard 5*4 or 20 Sq. Ft
Note on H31: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J31: The glazing is double pane but is broken or fogged and requires replacement.
Note on L31: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on N31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on P31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D32: This assumes both individual aluminum windows and storefront systems. Enter # of aluminum/steel windows. 1 window = a standard 5*4 or 20 Sq. Ft
Note on H32: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J32: The glazing is double pane but is broken or fogged and requires replacement.
Note on L32: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on N32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on P32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D33: This assumes a metal windows system clad with wood or vinyl. Enter # of clad windows. 1 window = a standard 5*4 or 20 Sq. Ft
Note on H33: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J33: The glazing is double pane but is broken or fogged and requires replacement.
Note on L33: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on N33: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on P33: Settlement or displacement is evident
Note on D34: Enter # of curtain wall windows. 1 window section = a standard 5*4 or 20 Sq. Ft
Note on H34: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J34: Minor leaks at wall seams - re-caulk and re-seal.
Note on L34: Window panels fogged and require replacement.
Note on N34: Settlement or displacement is evident.
Note on P34: Door frame, door, and hardware are damaged and require replacement
Note on D35: Apply to door count.
Note on H35: Door hardware is damaged or non-functional and requires repair only.
Note on J35: Door hardware is damaged or non-functional and requires replacement.
Note on L35: Door panel and hardware are damaged and require replacement.
Note on N35: Door frame, door, and hardware are damaged and require replacement.
Note on P35: Door frame, door, and hardware are damaged and require replacement
Note on D36: Apply to door count.
Note on H36: Door hardware is damaged or non-functional and requires repair only.
Note on J36: Door hardware is damaged or non-functional and requires replacement.
Note on L36: Door panel and hardware are damaged and require replacement.
Note on N36: Door frame, door, and hardware are damaged and require replacement.
Note on P36: Door frame, door, and hardware are damaged and require replacement
Note on D37: Apply to door count.
Note on H37: Minor Dings or Bends
Note on J37: Door hardware is damaged or non-functional and requires replacement.
Note on L37: Door panel and hardware are damaged and require replacement.
Note on N37: Door frame, door, and hardware are damaged and require replacement.
Note on D38: Apply to door count
Note on H38: Minor Dings or Bends
Note on J38: Door hardware is damaged or non-functional and requires replacement.
Note on L38: Door panel and hardware are damaged and require replacement.
Note on N38: Door track system, door panel, and hardware are damaged and require replacement.
Note on D39: Apply to door count
Note on H39: Minor Dings or Bends
Note on J39: Door hardware is damaged or non-functional and requires replacement.
Note on L39: Door panel and hardware are damaged and require replacement.
Note on N39: Door track system, door panel, and hardware are damaged and require replacement.
Note on C41: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts.
Note on H41: Small number of shingles lifting and/or separation in a portion of flashing.
Note on J41: Leaks in a specific area or zone related to poor detailing and or flashing.
Note on L41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on N41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on P41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on H42: Small number of shingles lifting and/or separation in a portion of flashing.
Note on J42: Leaks in a specific area or zone related to poor detailing and or flashing.
Note on L42: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on N42: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on P42: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on H43: Small number of shingles lifting and/or separation in a portion of flashing.
Note on J43: Leaks in a specific area or zone related to poor detailing and or flashing.
Note on L43: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on N43: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on H44: Minor tile cracking or seam seal deteriorating
Note on J44: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations.
Note on L44: Sections have lost their structural integrity and are separating causing water intrusion
Note on N44: Tiles are cracked, loose, or damaged and require removal and replacement.
Note on H45: Minor blistering requiring isolated patches.
Note on J45: Leaks in a specific area or zone related to poor detailing and or flashing or unchecked blisters.
Note on L45: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING.
Note on N45: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on H46: Minor blistering requiring isolated patches.
Note on J46: Leaks in a specific area or zone related to poor detailing and or flashing or seam separation.
Note on L46: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Prep and re-coat roof system OVER TOP OF EXISTING.
Note on N46: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND REPLACE roof system.
Note on P46: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on H47: Repair or replace caulking or seam seal
Note on J47: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant.
Note on L47: Sections are warping and leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing, panels and sealant.
Note on N47: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing.
Note on P47: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on H48: Minor tile cracking or seam seal deteriorating
Note on J48: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations.
Note on L48: Sections have lost their structural integrity and are separating causing water intrusion
Note on N48: Tiles are cracked, loose, or damaged and require removal and replacement.
Note on P48: Tiles are cracked, loose, or damaged and require removal and replacement
Note on D49: Based on building's gross square footage.
Note on H49: Minor leaking is occurring, requiring re-caulk and re-seal.
Note on J49: Minor leaking is occurring, requiring repair and re-caulk and re-seal.
Note on L49: Frame or glass is starting to loose its structural integrity requiring major repair.
Note on N49: The panes or framing are damaged beyond repair and requires replacement.
Note on P49: The panes or framing are damaged beyond repair and requires replacement
Note on D50: Apply to access hatch count.
Note on H50: Components are worn or damaged requiring repair
Note on J50: Components are damaged requiring replacement
Note on L50: Frame or hatch is starting to loose its structural integrity requiring repair
Note on N50: The door is non-functional or damaged beyond repair and requires replacement.
Note on P50: The door is non-functional or damaged beyond repair and requires replacement
Note on H53: Minor Damage not requiring replacement of frame
Note on J53: There are some sections which are damaged and requires a strategic repair
Note on L53: There are some sections which are damaged and requires a strategic removal and replacement
Note on N53: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on P53: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on H54: Minor Damage not requiring replacement of section
Note on J54: Cracking is evident which is affecting the wall construction
Note on L54: There are some blocks that are damaged and requires a strategic removal and replacement.
Note on N54: There is evidence of settling, failure, or a compromised structure that requires removal and replacement.
Note on P54: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on H55: Minor Damage not requiring replacement of frame
Note on J55: There are some sections which are damaged and requires a strategic removal and replacement
Note on L55: There is evidence of settling, failure, or a compromised structure that requires removal and replacement. Frame only no windows
Note on N55: There is evidence of settling, failure, or a compromised structure that requires removal and replacement. Including Windows
Note on P55: Door frame, door, and hardware are damaged and require replacement
Note on D56: Apply to door count.
Note on H56: Door hardware is functional but damaged requiring repair.
Note on J56: Door hardware is damaged or non-functional and requires replacement.
Note on L56: Door panel and hardware are damaged and require replacement.
Note on N56: Door frame, door, and hardware are damaged and require replacement.
Note on D57: Apply to door count.
Note on H57: Door hardware is functional but damaged requiring repair.
Note on J57: Door hardware is damaged or non-functional and requires replacement.
Note on L57: Door panel and hardware are damaged and require replacement.
Note on N57: Door frame, door, and hardware are damaged and require replacement.
Note on P57: Door frame, door, and hardware are damaged and require replacement
Note on D58: Apply to door count
Note on H58: Minor dings or bends
Note on J58: Door hardware is damaged or non-functional and requires replacement.
Note on L58: Door panel and hardware are damaged and require replacement.
Note on N58: Door frame, door, and hardware are damaged and require replacement.
Note on D59: Apply to door count
Note on H59: Minor Dings or Bends
Note on J59: Door hardware is damaged or non-functional and requires replacement.
Note on L59: Door panel and hardware are damaged and require replacement.
Note on N59: Door track system, door panel, and hardware are damaged and require replacement..
Note on D60: Apply to door count
Note on H60: Minor Dings or Bends
Note on J60: Door hardware is damaged or non-functional and requires replacement.
Note on L60: Door panel and hardware are damaged and require replacement.
Note on N60: Door track system, door panel, and hardware are damaged and require replacement.
Note on D61: Enter # of wood windows. 1 window = a standard 5*4 or 20 Sq. Ft
Note on H61: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J61: The glazing is double pane but is broken or fogged and requires replacement.
Note on L61: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on N61: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on D62: This assumes both individual aluminum windows and storefront systems. Enter # of aluminum/steel windows. 1 window = a standard 5*4 or 20 Sq. Ft
Note on H62: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J62: The glazing is double pane but is broken or fogged and requires replacement.
Note on L62: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on N62: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on P62: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D63: This assumes a metal windows system clad with wood or vinyl. Enter # of clad windows. 1 window = a standard 5*4 or 20 Sq. Ft
Note on H63: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on J63: The glazing is double pane but is broken or fogged and requires replacement.
Note on L63: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing.
Note on N63: The structural integrity of the frame is damaged, requiring the full replacement of the window unit.
Note on P63: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on P64: Settlement or displacement is evident
Note on D65: Apply to stair flights.
Note on E65: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H65: Minor patch and require required
Note on J65: Rails not compliant with code and require removal and replacement.
Note on L65: Sections are losing their structural integrity and repair major repair.
Note on N65: Structural integrity of stair unit is compromised and requires its removal and replacement.
Note on P65: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on D66: Apply to stair flights.
Note on E66: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PC
Note on H66: Rust visible - prep and re-finish.
Note on J66: Rails not compliant with code and require removal and replacement.
Note on L66: Sections are losing their structural integrity and repair major repair.
Note on N66: Structural integrity of stair unit is compromised and requires its removal and replacement.
Note on P66: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on D67: Apply to stair flights.
Note on E67: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H67: Minor patch and require required
Note on J67: An isolated structural crack or separation requiring re-enforcement in place.
Note on L67: Sections are losing their structural integrity and repair major repair.
Note on N67: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit.
Note on P67: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on D68: Apply to stair flights.
Note on E68: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H68: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on J68: Minor non structural cracking or chips requiring sealing
Note on L68: An isolated structural crack or separation requiring re-enforcement in place.
Note on N68: Severe cracking requiring removal and replacement of tread in fills.
Note on P68: Severe cracking requiring removal and replacement of tread in fills
Note on D69: Apply to stair flights.
Note on E69: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H69: Sporadic number of tiles are lifting or cracked/broken and require replacement.
Note on J69: Heaving, bubbling, or lifting in sections of the finish
Note on L69: The majority of tiles are lifting, cracking/broken and require replacement - the tiles or glue are NOT asbestos.
Note on N69: Finish is lifting or separating and creating trip hazards - remove and replace.
Note on P69: finish is lifting or separating and creating trip hazards - remove and replace
Note on D70: Apply to Stair Flights
Note on E70: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H70: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on J70: Heaving or lifting in sections of the finish
Note on L70: An isolated structural crack or separation requiring re-enforcement in place.
Note on N70: Finish is lifting or separating and creating trip hazards - remove and replace.
Note on D71: Apply to Stair Flights
Note on E71: For data collected in the App prior to 2/1/2022: Verify all STAIR fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H71: Some sections are beginning to lift or rust
Note on J71: Rusting non structural cracks or breaks requiring repair
Note on L71: Isolated structural cracks or breaks requiring repair
Note on N71: Structural integrity as been compromised requiring replacement
Note on H73: Surface is in tact but finish is deteriorated - paint.
Note on J73: Surface is damaged - patching of the surface is required prior to painting.
Note on L73: Cracks visible - route and patch prior to painting.
Note on N73: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P73: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on H74: Surface is in tact but finish is deteriorated - paint.
Note on J74: Surface is damaged - patching of the surface is required prior to painting.
Note on L74: Cracks visible - route and patch prior to painting.
Note on N74: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P74: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on H75: Surface is in tact but finish is deteriorated - paint.
Note on J75: Surface is damaged - patching of the surface is required prior to painting.
Note on L75: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on N75: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P75: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on H76: Surface is in tact but finish is deteriorated - paint/repair.
Note on J76: Surface is damaged - patching of the surface is required prior to painting.
Note on L76: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on N76: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P76: Tiles are cracked or in disrepair
Note on H77: Surface is in tact but finish is deteriorated - paint/repair.
Note on J77: Surface is damaged - patching of the surface is required prior to painting.
Note on L77: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on N77: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on H78: Surface is in tact but finish is deteriorated - paint/repair.
Note on J78: Surface is damaged - patching of the surface is required prior to painting.
Note on L78: A number of panels are damaged, requiring patch and repair prior to re-painting.
Note on N78: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on H79: Grout is damaged or deteriorated.
Note on J79: Surface is damaged - patching of the surface is required.
Note on L79: A number of tiles are damaged or missing requiring repair and replace of sections
Note on N79: Tiles are cracked or in disrepair.
Note on H80: Sporadic number of sections are worn down to pad.
Note on J80: Sporadic number of sections are worn and tearing through to pad requiring repair
Note on L80: Worn or stained or starting to pull up/bubble requiring sections to be replaced
Note on N80: Worn or severely stained or starting to pull up/bubble requiring full replacement.
Note on P80: worn or severely stained or starting to pull up / bubble
Note on H81: Sporadic number of tiles are lifting or cracked/broken and require replacement.
Note on J81: Sections of tiles are lifting, cracking/broken and require repair or replacement in those sections- the tiles or glue are NOT asbestos.
Note on L81: The majority of tiles are lifting, cracking/broken and require replacement - the tiles or glue are NOT asbestos.
Note on N81: The majority of tiles are lifting, cracking/broken and require replacement - the tiles or glue are asbestos.
Note on P81: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on H82: Sections are starting to show signs of wear requiring maintenance
Note on J82: Sporadic sections are damaged and require repair
Note on L82: Sections are worn or seams separating are separating - repair and replace section only.
Note on N82: Severely worn or seams separating - replace.
Note on P82: Severely worn or seams separating - replace
Note on H83: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal.
Note on J83: Sporadic sections are damaged and patch and seal
Note on L83: Damaged areas or hairline cracking, but not differential - requires patch and seal
Note on N83: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above.
Note on P83: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on H84: Grout is damaged or deteriorated.
Note on J84: Sporadic sections are damaged and require repair or replacement tiles in those locations
Note on L84: Sections of tile are damaged requiring full repair and replace
Note on N84: Tiles are cracked or in disrepair requiring full removal and leveling of surface and retile
Note on P84: Tiles are cracked or in disrepair
Note on H85: Sections are starting to show signs of wear requiring maintenance
Note on J85: Sporadic sections are damaged and require repair
Note on L85: Sections are bubbling or cracking requiring prep and patch
Note on N85: Systemic blistering or severely worn traffic areas - strip and replace.
Note on P85: Systemic blistering or severely worn traffic areas - strip and replace
Note on H86: Sections are starting to show signs of wear requiring maintenance
Note on J86: Surface is damaged - requires sanding, repair, and re-coat/re-stripe.
Note on L86: Sections are starting to warp or cup requiring those sections to be repaired or replaced
Note on N86: Wood planks are deteriorated, separating, and multiple dead spots - replace floor.
Note on P86: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on H87: Surface is in tact but finish is deteriorated - paint.
Note on J87: Surface is damaged - patching of the surface is required prior to painting.
Note on L87: Cracks visible - route and patch prior to painting.
Note on N87: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P87: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on H88: Stained or damaged ceiling tiles.
Note on J88: Diagonal bracing missing from grid.
Note on L88: Tiles are sagging or grid is shifting in sections
Note on N88: Grid is sagging with tiles compromised - requires replacement of system.
Note on P88: Grid is sagging with tiles compromised - requires replacement of system
Note on H89: Stained or damaged ceiling tiles.
Note on J89: Panels are damaged with sections chipped or removed
Note on L89: Tiles are sagging or adhesive is delaminating from panel
Note on N89: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P89: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on H90: Stained or damaged ceiling tiles.
Note on J90: Panels are damaged with sections chipped or removed
Note on L90: Tiles are sagging or adhesive is delaminating from panel
Note on N90: Systemic failure of finish, possible water intrusion - requires removal and replacement.
Note on P90: Surface is in tact but finish is deteriorated - paint
Note on H91: Surface is in tact but finish is deteriorated - paint.
Note on J91: Surface is damaged requiring repair prior to repaint
Note on L91: Surface is cracked or damaged requiring major repairs.
Note on N91: Surface damaged with possible water intrusion. Replace
Note on C94: Assume standard cab-style elevator. Apply per stop.
Note on E94: Insert number of elevators * number of stories, i.e. if there are 2 elevators each going 3 stories - insert 6. For data collected in the App prior to 2/1/2022: Verify all CONVEYING fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H94: The elevator doors are damaged and require replacement.
Note on J94: Electrical components are not working.
Note on L94: Replacement of the hoist cables, guide rails, or other similar mechanical components is required.
Note on N94: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on P94: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C95: Apply per flight.
Note on E95: Insert number of escalators * number of stories - i.e. if there are 2 escalators each going 3 stories - insert 6 For data collected in the App prior to 2/1/2022: Verify all CONVEYING fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H95: Mechanical Components are not working requiring repair
Note on J95: Electrical components are not working.
Note on L95: Major mechanical or electrical systems requires repair
Note on N95: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on P95: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C96: Assume open vertical or inclined lift. Apply per unit.
Note on E96: Insert number of lifts. For data collected in the App prior to 2/1/2022: Verify all CONVEYING fields are filled in on the CONSTRUCTION tab and then re-run PCA.
Note on H96: Mechanical Components are not working requiring repair
Note on J96: Electrical components are not working.
Note on L96: Major mechanical or electrical systems requires repair
Note on N96: Mechanical and electrical components have deteriorated requiring the replacement of the system.
Note on P96: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C98: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here.
Note on D98: Enter number of units. If units fall in multiple categories use a range and make good notes.
Note on E98: Inset Number of Units
Note on H98: Fixture Components are functional but broken or worn requiring repair or replacement.
Note on J98: Fixture components (Flush valves or faucets) are non-functional and require repair.
Note on L98: A minor fixture (Faucet, spigot, maintenance tub, shower fixture) itself is broken or is not compliant with water efficiency standards.
Note on N98: A major fixture (sink, urinal, toilet, drinking fountain) itself is broken or is not compliant with water efficiency standards.
Note on P98: The fixture itself is broken or is not compliant with water efficiency standards
Note on H99: The vale stems, pressure gauges, and gate valves no longer function.
Note on J99: The insulation on the piping is in disrepair, loose, or missing.
Note on L99: Section of piping are damaged and require replacement
Note on N99: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on P99: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on H100: In some areas, the floor or wall, clean outs or floor drains require repair
Note on J100: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains.
Note on L100: Sections of piping are damaged and require replacement
Note on N100: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement.
Note on P100: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on C101: This is for the presence of interior rain drains. Excludes external downspouts. Based on gross square footage.
Note on H101: Weather seal is worn requires replacement
Note on J101: The rain drain or overflow is damaged and needs replacement.
Note on L101: The rain drain housing is showing signs of deterioration and movement within the roofing structure requiring major repair
Note on N101: The integrity of the piping is compromised and is leaking inside the walls.
Note on P101: The integrity of the piping is compromised and is leaking inside the walls
Note on C104: This assumes gas piping.
Note on H104: The valve stems, riser gate valves, and temperature probes need to be maintenance
Note on J104: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on L104: Sections of piping are damaged and require replacement
Note on N104: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on P104: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on E105: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H105: The burner is inefficient and requires refurbishment.
Note on J105: One major component needs to be replaced.
Note on L105: More than one major component needs to be replaced.
Note on N105: The system is in failure.
Note on P105: The system is in failure
Note on E106: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H106: A small number of minor parts need to be repaired or replaced.
Note on J106: One major component needs to be replaced
Note on L106: Some of the distribution fans and coils are dysfunctional.
Note on N106: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair.
Note on P106: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on E107: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H107: A small number of minor parts need to be repaired or replaced.
Note on J107: One major component needs to be replaced
Note on L107: The burner, combustion chamber, or fan are faulty and require replacement.
Note on N107: The entire furnace requires replacement.
Note on P107: The entire furnace requires replacement
Note on E108: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H108: A small number of minor parts need to be repaired or replaced.
Note on J108: One major component needs to be replaced
Note on L108: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger.
Note on N108: System operates at low efficiency with corrosion and leaks apparent. Replace system.
Note on P108: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on E109: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H109: A small number of minor parts need to be repaired or replaced.
Note on J109: One major component needs to be replaced.
Note on L109: Some of the distribution fans and coils are dysfunctional.
Note on N109: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair.
Note on P109: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on E110: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H110: A small number of minor parts need to be repaired or replaced.
Note on J110: One major component needs to be replaced.
Note on L110: Multiple electrical or mechanical components require replacement
Note on N110: The chiller is beyond economic repair.
Note on P110: The chiller is beyond economic repair
Note on E111: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H111: Seams require retaping for repair
Note on J111: Dampers in the system are inoperative.
Note on L111: The insulation is damaged or missing.
Note on N111: The ductwork is damaged or inadequately designed and requires replacement.
Note on P111: The ductwork is damaged or inadequately designed and requires replacement
Note on E112: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H112: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on J112: The insulation on the piping is in disrepair, loose, or missing.
Note on L112: Sections of piping are damaged and require replacement
Note on N112: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves.
Note on P112: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on E113: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H113: A small number of minor parts need to be repaired or replaced.
Note on J113: One major component needs to be replaced.
Note on L113: Multiple electrical or mechanical components require replacement
Note on N113: Entire unit is failing to function.
Note on P113: Entire unit is failing to function
Note on E114: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H114: Minor components are worn or damaged requiring repair or replacement
Note on J114: Internal compressor is bad and requires repair.
Note on L114: Internal compressor is bad and requires replacement.
Note on N114: Entire unit is failing to function.
Note on P114: Entire unit is failing to function
Note on E115: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on H115: Minor components are worn or damaged requiring repair or replacement
Note on J115: In-room valve is failing and requires replacement.
Note on L115: One major component needs to be replaced.
Note on N115: Entire unit is failing to function.
Note on P115: Entire unit is failing to function
Note on H116: Minor components are worn or damaged requiring repair or replacement
Note on J116: System experiences electrical issues requiring repair
Note on L116: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators.
Note on N116: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older/obsolete pneumatic system - replace.
Note on P116: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on E117: Tiffany Hammond: App does not calculate this value; must enter manually.
Note on N117: One or more zones require re-balancing.
Note on P117: One or more zones require re-balancing
Note on H120: Valves, couplers, connectors showing signs of corrosion requiring repair
Note on J120: Sprinkler heads are inoperable or non-compliant and need to be replaced.
Note on L120: Sections of piping are damaged requiring repair.
Note on N120: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads.
Note on P120: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on H121: Valves, couplers, connectors showing signs of corrosion requiring repair
Note on J121: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced.
Note on L121: Sections of piping are damaged requiring repair.
Note on N121: The fire pump is beyond repair and needs to be replaced.
Note on P121: The fire pump is beyond repair and needs to be replaced
Note on C122: Assume chemical extinguishing system.
Note on H122: Components of the system require maintenance or repair
Note on J122: The back-up tank has been discharged or lacks pressure and needs to be replaced.
Note on L122: The back-up tank has been discharged or lacks pressure and needs to be replaced AND components need to repaired
Note on N122: The system is non-functional or not compliant with the current needs and needs to be replaced.
Note on P122: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on H125: Sections of wiring have been damaged requiring repair
Note on J125: Wiring has systemic problems or does not meet code and needs to be replaced.
Note on L125: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement.
Note on N125: Main switchgear is obsolete or undersized and requires replacement, including service into building.
Note on P125: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on H126: Sections of wiring have been damaged requiring repair
Note on J126: Wiring has systemic problems or does not meet code and needs to be replaced.
Note on L126: The lighting fixtures are obsolete or non-functional and require replacement.
Note on N126: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring.
Note on P126: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on H127: Minor components are worn or damaged requiring repair or replacement
Note on J127: There are individual devices that are not functional.
Note on L127: The master control panel is obsolete or not functional.
Note on N127: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on P127: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H128: Minor components are worn or damaged requiring repair or replacement
Note on J128: There are individual devices that are not functional.
Note on L128: The master control panel is obsolete or not functional.
Note on N128: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on P128: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H129: Minor components are worn or damaged requiring repair or replacement
Note on J129: There are individual devices that are not functional.
Note on L129: The master control panel is obsolete or not functional.
Note on N129: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on P129: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H130: Minor components are worn or damaged requiring repair or replacement
Note on J130: There are individual devices that are not functional.
Note on L130: The master control panel is obsolete or not functional.
Note on N130: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on P130: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H131: Minor components are worn or damaged requiring repair or replacement
Note on J131: There are individual devices that are not functional.
Note on L131: The master control panel is obsolete or not functional.
Note on N131: The system is obsolete or works intermittently in multiple areas and requires a system replacement.
Note on P131: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H132: Minor components are worn or damaged requiring repair or replacement
Note on J132: There are individual devices that are not functional or in regular alarm.
Note on L132: The master control panel is obsolete or not functional.
Note on N132: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system.
Note on P132: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on H133: Individual room sensors are failing and require replacement.
Note on J133: There are individual devices that are not functional.
Note on L133: The central control panel and software need upgraded.
Note on N133: The entire system is in failure and requires replacement of sensors, wiring and central panel.
Note on P133: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on H137: 2-3 pieces of equipment require replacement.
Note on J137: Counters and sinks are not code compliant and require replacement with stainless steel and sink system.
Note on L137: Walk-in cooler and freezer are not functional or function intermittently and require replacement.
Note on N137: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen.
Note on P137: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on H138: 2-3 pieces of equipment require repair.
Note on J138: 2-3 pieces of equipment require replacement.
Note on L138: Mechanical and electrical service upgrades are required to meet code and amount of program equipment.
Note on N138: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code.
Note on P138: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on E139: Enter total square feet of science classrooms.
Note on H139: Minor repairs required to stationary equipment
Note on J139: Room lacking (and needing) eye wash or fume hood.
Note on L139: Sinks are in disrepair and require replacement.
Note on N139: Work stations need upgrades to meet current program criteria - replace.
Note on P139: Work stations need upgrades to meet current program criteria - replace
Note on E140: Enter total square feet of art classrooms.
Note on H140: Minor repairs required to stationary equipment
Note on J140: Storage units damaged or in disrepair.
Note on L140: Sinks are in disrepair and require replacement.
Note on N140: Work stations need upgrades to meet current program criteria - replace.
Note on P140: Work stations need upgrades to meet current program criteria - replace
Note on C141: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: there was a slight formatting difference b/t this and the label in the PCA cost table: changed to the PCA cost table language
Note on E141: Insert square feet of auditorium. If multi-purpose room, enter square feet of stage area only. Assumes stage with rigging and lighting.
Note on H141: Casework and other stationary pieces of equipment require repair.
Note on J141: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded.
Note on L141: Fly rigging in disrepair and needs upgrading.
Note on N141: 2 or more stage system dysfunctional and needs upgrade/replacement to production systems.
Note on P141: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on H142: An accessory is damaged or missing
Note on J142: Accessories need to be replaced to meet ADA
Note on L142: The stall doors are not functional or missing and need to be replaced.
Note on N142: The restrooms stall structure is failing or needs re-configuration and needs to be replaced.
Note on P142: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on D143: Note anything specific in the "Other" category at the bottom of the assessment form
Note on C146: Assume fixed casework (counters, cabinets, shelving, etc.).
Note on H146: The counter top or exposed surface has been damaged and can be refinished.
Note on J146: The drawers and/or doors are damaged and require replacement including hardware.
Note on L146: A combination of minor and moderate action is required, but the cabinet box is still salvageable.
Note on N146: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced.
Note on P146: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on C147: Assume loose furnishings (desks, chairs, tables, etc.).
Note on H147: Some pieces of furnishings require repair
Note on N147: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement.
Note on P147: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on C152: Paved only or needs to be paved. Apply to surface area.
Note on E152: Indicate square footage of road.
Note on H152: Minor cracking exists and can be resolved with application of a slurry coat.
Note on J152: Moderate cracking exists and can be resolved with application of a slurry coat and moderate leveling
Note on L152: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated.
Note on N152: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category should be used.
Note on P152: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on C153: Paved only or needs to be paved. Apply to surface area.
Note on E153: Indicate square footage of parking lot.
Note on H153: Minor cracking exists and can be resolved with application of a slurry coat.
Note on J153: Moderate cracking exists and can be resolved with application of a slurry coat and moderate leveling
Note on L153: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated.
Note on N153: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used.
Note on P153: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on C154: Concrete only or needs to be concrete. Apply to surface area.
Note on E154: Indicate square footage of walks and plazas.
Note on H154: Minor cracking observed, patch and seal
Note on J154: Cracking as a result of heaving
Note on L154: Sections are broken with differential settlement requiring the removal of the effected panels and replacement.
Note on N154: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used.
Note on P154: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on C155: Chain-link fencing. Apply to LF of fence.
Note on E155: Indicate length of fencing. Assuming 6' high chain-link.
Note on H155: Chain link or couplers damaged
Note on J155: The fence fabric is damaged and needs to be replaced.
Note on L155: Section of fence is damaged requiring replacement
Note on N155: The fencing has lost its structural integrity and is beyond repair.
Note on P155: The fencing has lost its structural integrity and is beyond repair.
Note on C156: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form. Apply to landscape area.
Note on E156: Indicate square footage of landscaped area served (including grass areas).
Note on H156: Watering heads require replacement
Note on J156: Sections of water lines are damaged requiring section to be replaced.
Note on L156: Sections are not balanced correctly
Note on N156: Irrigation system is dysfunctional and beyond repair.
Note on P156: Irrigation system is dysfunctional and beyond repair
Note on D158: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form. Apply to surface area.
Note on N158: A portion of the line has lost its structural integrity and requires replacement.
Note on P158: A portion of the line has lost its structural integrity and requires replacement
Note on D159: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form. Apply to surface area.
Note on N159: A portion of the line has lost its structural integrity and requires replacement.
Note on P159: A portion of the line has lost its structural integrity and requires replacement
Note on C160: Apply to surface area. Lines only. Septic fields, tanks, etc. should be placed in "Other" category at bottom of form.
Note on N160: A portion of the line has lost its structural integrity and requires replacement.
Note on P160: A portion of the line has lost its structural integrity and requires replacement
Note on C161: Apply to surface area. Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form.
Note on H161: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign.
Note on J161: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Note on L161: Detention/retention has failed, but piping and catch basins are functional. Replace detention/retention system.
Note on N161: The entire underground system has failed and requires removal and replacement of all components.
Note on P161: The entire underground system has failed and requires removal and replacement of all components
Note on C162: Apply to surface area.
Note on N162: A portion of the line has lost its structural integrity and requires replacement.
Note on P162: A portion of the line has lost its structural integrity and requires replacement
Note on C163: Apply to surface area.
Note on N163: A portion of the line has lost its structural integrity and requires replacement.
Note on P163: A portion of the line has lost its structural integrity and requires replacement
Note on C164: Apply to surface area. Natural gas lines.
Note on N164: A portion of the line has lost its structural integrity and requires replacement.
Note on P164: A portion of the line has lost its structural integrity and requires replacement
Note on D167: Assumes the private portion of the service lines typically underground after the meter or transformer. Apply to surface area.
Note on L167: The transformer no longer functions and is in need of replacement.
Note on N167: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines.
Note on P167: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on D168: Apply to generator quantity.
Note on H168: The generator needs to be tuned up.
Note on J168: The valves or other engine parts need to be repaired or replaced and then a tune up.
Note on L168: Generator is non-functional or under-sized.
Note on N168: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized.
Note on P168: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on C169: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: This was called "exterior site (pole) lighting here but labeled "site lighting" in the PCA cost table. Changed to the simplier language in the PCA cost table
Note on E169: Tiffany Hammond: Enter total number of exterior site lights
Note on H169: The fixtures are nonfunctional and require replacement.
Note on N169: The fixtures, supports, and underground wiring need to be replaced.
Note on P169: The fixtures, supports, and underground wiring need to be replaced
Note on C170: Assumes low voltage lines underground.
Note on N170: Site cabling is inadequate or service is interrupted - replace cabling.
Note on P170: Site cabling is inadequate or service is interrupted - replace cabling
Note on C174: For assessment professional to hand enter for specialty items and systems that do not fit into categories above
Note on C210: Describe in detail any safety or security improvements needed at this site.
Note on C223: Populated from the Portable Classrooms fields in the Renovations, Additions & Prtbls

## Rollup_PCA_notes (hidden)
LOOKUP KEY | % of Building or Number | None | Minor | Moderate | Major | Replace as part of Renovation | Replace as singular scope | % of System or Finish | Automated Budget Estimate | Notes | MFI Cateogory | Unit | CRV | Unit FCI | Unit Green/Yellow/Red | Major/Replace | Minor/Moderate | LOOKUP |  |  | 1 | 5 | 4 | 3 | 2
B2030 Exterior Doors_Hollow Metal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | B2030 | Exterior Metal Hollow Doors | Exterior Metal Hollow Doors | Exterior | Doors | Hollow | Metal
B2030 Exterior Doors_Overhead Metal Garage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | B2030 | Exterior Garage Metal Overhead Doors | Exterior Garage Metal Overhead Doors | Exterior | Doors | Overhead | Metal | Garage
B2030 Exterior Doors_Rollup Metal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | B2030 | Exterior Metal Rollup Doors | Exterior Metal Rollup Doors | Exterior | Doors | Rollup | Metal
B2030 Exterior Doors_Storefront | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | B2030 | Exterior Storefront Doors | Exterior Storefront Doors | Exterior | Doors | Storefront
B2030 Exterior Doors_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | B2030 | Exterior Wood Doors | Exterior Wood Doors | Exterior | Doors | Wood
C1020 Interior Doors_Hollow Metal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | C1020 | Interior Metal Hollow Doors | Interior Metal Hollow Doors | Interior | Doors | Hollow | Metal
C1020 Interior Doors_Overhead Metal Garage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | C1020 | Interior Garage Metal Overhead Doors | Interior Garage Metal Overhead Doors | Interior | Doors | Overhead | Metal | Garage
C1020 Interior Doors_Rollup Metal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | C1020 | Interior Metal Rollup Doors | Interior Metal Rollup Doors | Interior | Doors | Rollup | Metal
C1020 Interior Doors_Storefront | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | C1020 | Interior Storefront Doors | Interior Storefront Doors | Interior | Doors | Storefront
C1020 Interior Doors_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Doors | Unit | 0 | 0% | Green |  |  | C1020 | Interior Wood Doors | Interior Wood Doors | Interior | Doors | Wood
D5010 Electrical Service & Distribution_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5010 | Electrical Distribution & Service | Electrical Distribution & Service | Electrical | Service |  | & | Distribution
D5020 Lighting and Branch Wiring_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5020 | Lighting Branch Wiring | Lighting Branch Wiring | Lighting |  |  | Wiring | Branch
G4010 Electrical Distribution_Generator | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | Unit | 0 | 0% | Green |  |  | G4010 | Electrical Generator Distribution | Electrical Generator Distribution | Electrical | Distribution | Generator
G4010 Electrical Distribution_Service | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | G4010 | Electrical Service Distribution | Electrical Service Distribution | Electrical | Distribution | Service
G4020 Site Lighting_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | Unit | 0 | 0% | Green |  |  | G4020 | Exterior Site Lighting | Exterior Site Lighting | Exterior |  |  | Lighting | Site
B2010 Exterior Walls_Concrete Formed / Tilt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior Structure | SF | 0 | 0% | Green |  |  | B2010 | Exterior / Formed Concrete Walls | Exterior / Formed Concrete Walls | Exterior | Walls | Concrete | Formed | / | Tilt
B2010 Exterior Walls_Framed w/ Wood Siding | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior Structure | SF | 0 | 0% | Green |  |  | B2010 | Exterior Wood w/ Framed Walls | Exterior Wood w/ Framed Walls | Exterior | Walls | Framed | w/ | Wood | Siding
B2010 Exterior Walls_Framed w/Masonry Veneer | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior Structure | SF | 0 | 0% | Green |  |  | B2010 | Exterior Veneer w/Masonry Framed Walls | Exterior Veneer w/Masonry Framed Walls | Exterior | Walls | Framed | w/Masonry | Veneer
B2010 Exterior Walls_Framed w/Metal Panel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior Structure | SF | 0 | 0% | Green |  |  | B2010 | Exterior Panel w/Metal Framed Walls | Exterior Panel w/Metal Framed Walls | Exterior | Walls | Framed | w/Metal | Panel
B2010 Exterior Walls_Framed w/Stucco | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior Structure | SF | 0 | 0% | Green |  |  | B2010 | Exterior w/Stucco Framed Walls | Exterior w/Stucco Framed Walls | Exterior | Walls | Framed | w/Stucco
B2010 Exterior Walls_Masonry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior Structure | SF | 0 | 0% | Green |  |  | B2010 | Exterior Masonry Walls | Exterior Masonry Walls | Exterior | Walls | Masonry
B2020 Exterior Windows_Aluminum/Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | B2020 | Exterior Aluminum/Steel Windows | Exterior Aluminum/Steel Windows | Exterior | Windows | Aluminum/Steel
B2020 Exterior Windows_Clad | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | B2020 | Exterior Clad Windows | Exterior Clad Windows | Exterior | Windows | Clad
B2020 Exterior Windows_Curtain Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | B2020 | Exterior Wall Curtain Windows | Exterior Wall Curtain Windows | Exterior | Windows | Curtain | Wall
B2020 Exterior Windows_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | B2020 | Exterior Wood Windows | Exterior Wood Windows | Exterior | Windows | Wood
Interior Windows_Aluminum/Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | Interior | Windows (Aluminum/Steel) | Windows (Aluminum/Steel) | Windows (Aluminum/Steel)
Interior Windows_Clad | 1 | 0 | Insert an estimated local cost inflation factor based on how much local costs are greater/lesser than the base prices in the PCA Cost Tables. (E.g., 1.15 = costs are ~ 15% greater than the average in the PCA Cost Table. If costs are considered average, keep the value "1") | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | Interior | Windows (Clad) | Windows (Clad) | Windows (Clad)
Interior Windows_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Exterior/Interior Windows | Unit | 0 | 0% | Green |  |  | Interior | Windows (Wood) | Windows (Wood) | Windows (Wood)
B1010 Floor Construction_Concrete | 0 | 0 | Name of the company performing the assessment | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | B1010 | Floor Concrete Construction | Floor Concrete Construction | Floor | Construction | Concrete
B1010 Floor Construction_Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | B1010 | Floor Steel Construction | Floor Steel Construction | Floor | Construction | Steel
B1010 Floor Construction_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | B1010 | Floor Wood Construction | Floor Wood Construction | Floor | Construction | Wood
B1020 Roof Construction_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B1020 | Roof Wood Construction | Roof Wood Construction | Roof | Construction | Wood
C3020 Floor Finishes_Carpet / Soft Surface | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Carpet Finishes | Floor Carpet Finishes | Floor | Finishes | Carpet
C3020 Floor Finishes_Ceramic Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Tile Ceramic Finishes | Floor Tile Ceramic Finishes | Floor | Finishes | Ceramic | Tile
C3020 Floor Finishes_Liquid Applied | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Applied Liquid Finishes | Floor Applied Liquid Finishes | Floor | Finishes | Liquid | Applied
C3020 Floor Finishes_Polished Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Concrete Polished Finishes | Floor Concrete Polished Finishes | Floor | Finishes | Polished | Concrete
C3020 Floor Finishes_Resilient Sheet | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Sheet Resilient Finishes | Floor Sheet Resilient Finishes | Floor | Finishes | Resilient | Sheet
C3020 Floor Finishes_Resilient Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Tile Resilient Finishes | Floor Tile Resilient Finishes | Floor | Finishes | Resilient | Tile
C3020 Floor Finishes_Wood Sports Floor | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Flooring | SF | 0 | 0% | Green |  |  | C3020 | Floor Sports floor Wood Finishes | Floor Sports floor Wood Finishes | Floor | Finishes | Wood | Sports floor
A1010 Standard Foundations_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Foundation | SF | 0 | 0% | Green |  |  | A1010 | Standard Foundations | Standard Foundations | Standard | Foundations
A1020 Special Foundations_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Foundation | SF | 0 | 0% | Green |  |  | A1020 | Special Foundations | Special Foundations | Special | Foundations
A1030 Slab on Grade_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Foundation | SF | 0 | 0% | Green |  |  | A1030 | Slab on Masonry Grade | Slab on Masonry Grade | Slab | Grade |  | on Masonry
A2020 Basement Walls_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Foundation | SF | 0 | 0% | Green |  |  | A2020 | Basement Walls | Basement Walls | Basement | Walls
E1010 Commercial Equipment_Food Service | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | SF | 0 | 0% | Green |  |  | E1010 | Commercial Service Food Equipment | Commercial Service Food Equipment | Commercial | Equipment | Food | Service
E1010 Commercial Equipment_Vocational | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | SF | 0 | 0% | Green |  |  | E1010 | Commercial Vocational Equipment | Commercial Vocational Equipment | Commercial | Equipment | Vocational
E1020 Institutional Equipment_Art | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | Unit | 0 | 0% | Green |  |  | E1020 | Institutional Art Equipment | Institutional Art Equipment | Institutional | Equipment | Art
E1020 Institutional Equipment_Restroom Accessories/Stalls | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | SF | 0 | 0% | Green |  |  | E1020 | Institutional Accessories/Stalls Restroom Equipment | Institutional Accessories/Stalls Restroom Equipment | Institutional | Equipment | Restroom | Accessories/Stalls
E1020 Institutional Equipment_Science | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | Unit | 0 | 0% | Green |  |  | E1020 | Institutional Science Equipment | Institutional Science Equipment | Institutional | Equipment | Science
E1020 Institutional Equipment_Stage Performance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | Unit | 0 | 0% | Green |  |  | E1020 | Institutional Performance Stage Equipment | Institutional Performance Stage Equipment | Institutional | Equipment | Stage | Performance
E2010 Fixed Furnishings_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | SF | 0 | 0% | Green |  |  | E2010 | Fixed Furnishings | Fixed Furnishings | Fixed | Furnishings
E2020 Movable Furnishings_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Furnishing, Fixtures, Equipment | SF | 0 | 0% | Green |  |  | E2020 | Movable Furnishings | Movable Furnishings | Movable | Furnishings
D3010 Energy Supply_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3010 | Energy Supply | Energy Supply | Energy | Supply
D3020 Heat Generating Systems_Air Handler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3020 | Heat air handler Systems | Heat air handler Systems | Heat |  |  | Systems | air handler
D3020 Heat Generating Systems_Boiler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3020 | Heat boiler Systems | Heat boiler Systems | Heat |  |  | Systems | boiler
D3020 Heat Generating Systems_Furnace | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3020 | Heat furnace Systems | Heat furnace Systems | Heat |  |  | Systems | furnace
D3020 Heat Generating Systems_Heat Exchanger | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3020 | Heat heat exchanger Systems | Heat heat exchanger Systems | Heat |  |  | Systems | heat exchanger
D3030 Cooling Generating Systems_Component of air handler | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3030 | Cooling component of air handler Systems | Cooling component of air handler Systems | Cooling |  |  | Systems | component of air handler
D3030 Cooling Generating Systems_Stand alone chiller | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3030 | Cooling Stand alone chiller Systems | Cooling Stand alone chiller Systems | Cooling |  |  | Systems | Stand alone chiller | chiller
D3040 Distribution Systems_Ductwork | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3040 | Distribution Ductwork Systems | Distribution Ductwork Systems | Distribution | Systems | Ductwork
D3040 Distribution Systems_Hot water return & supply | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3040 | Distribution water return & supply Hot Systems | Distribution water return & supply Hot Systems | Distribution | Systems | Hot | water return & supply
D3050 Terminal & Package Units_Above ceiling VAV unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3050 | Terminal Package VAV unit ceiling | Terminal Package VAV unit ceiling | Terminal | ceiling | VAV unit | Package
D3050 Terminal & Package Units_In-room radiant unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3050 | Terminal Package unit radiant | Terminal Package unit radiant | Terminal | radiant | unit | Package
D3050 Terminal & Package Units_In-room ventilator unit | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3050 | Terminal Package unit ventilator | Terminal Package unit ventilator | Terminal | ventilator | unit | Package
D3060 Controls & Instrumentation_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3060 | Controls Instrumentation | Controls Instrumentation | Controls |  |  | Instrumentation
D3070 Systems Testing & Balancing_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | HVAC | SF | 0 | 0% | Green |  |  | D3070 | Systems & Balancing Testing | Systems & Balancing Testing | Systems | Testing |  | & Balancing
C1010 Partitions_Curtain Wall | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C1010 | Partitions (Curtain) Wall | Partitions (Curtain) Wall | Partitions (Curtain) | Wall
C1010 Partitions_Framed | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C1010 | Partitions (Framed) | Partitions (Framed) | Partitions (Framed)
C1010 Partitions_Masonry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C1010 | Partitions (Masonry) | Partitions (Masonry) | Partitions (Masonry)
C2010 Stair Construction_Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2010 | Stair Concrete Construction | Stair Concrete Construction | Stair | Construction | Concrete
C2010 Stair Construction_Metal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2010 | Stair Metal Construction | Stair Metal Construction | Stair | Construction | Metal
C2010 Stair Construction_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2010 | Stair Wood Construction | Stair Wood Construction | Stair | Construction | Wood
C2020 Stair Finishes_Concrete Fill | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2020 | Stair Fill Concrete Finishes | Stair Fill Concrete Finishes | Stair | Finishes | Concrete | Fill
C2020 Stair Finishes_Metal Grating | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2020 | Stair Grating Metal Finishes | Stair Grating Metal Finishes | Stair | Finishes | Metal | Grating
C2020 Stair Finishes_Resilient | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2020 | Stair Resilient Finishes | Stair Resilient Finishes | Stair | Finishes | Resilient
C2020 Stair Finishes_Wood | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | C2020 | Stair Wood Finishes | Stair Wood Finishes | Stair | Finishes | Wood
C3010 Wall Finishes_Ceramic Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wall Tile Ceramic Finishes | Wall Tile Ceramic Finishes | Wall | Finishes | Ceramic | Tile
C3010 Wall Finishes_Formica | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wall Formica Finishes | Wall Formica Finishes | Wall | Finishes | Formica
C3010 Wall Finishes_Paint on Masonry | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wall on Masonry Paint Finishes | Wall on Masonry Paint Finishes | Wall | Finishes | Paint | on Masonry
C3010 Wall Finishes_Vinyl Paneling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wall Paneling Vinyl Finishes | Wall Paneling Vinyl Finishes | Wall | Finishes | Vinyl | Paneling
C3010 Wall Finishes_Wainscot | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wainscot Finishes | Wainscot Finishes |  | Finishes | Wainscot
C3010 Wall Finishes_Wallboard | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wallboard Finishes | Wallboard Finishes |  | Finishes | Wallboard
C3010 Wall Finishes_Wood Paneling | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3010 | Wall Paneling Wood Finishes | Wall Paneling Wood Finishes | Wall | Finishes | Wood | Paneling
C3030 Ceiling Finishes_Glued-Up Ceiling Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3030 | Ceiling Glued-Up Finishes | Ceiling Glued-Up Finishes | Ceiling | Finishes | Glued-Up
C3030 Ceiling Finishes_Lay-In Ceiling Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3030 | Ceiling Lay-In Finishes | Ceiling Lay-In Finishes | Ceiling | Finishes | Lay-In
C3030 Ceiling Finishes_Painted Structure | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3030 | Ceiling Structure Painted Finishes | Ceiling Structure Painted Finishes | Ceiling | Finishes | Painted | Structure
C3030 Ceiling Finishes_Tectum | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3030 | Ceiling Tectum Finishes | Ceiling Tectum Finishes | Ceiling | Finishes | Tectum
C3030 Ceiling Finishes_Wallboard | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | SF | 0 | 0% | Green |  |  | C3030 | Ceiling Wallboard Finishes | Ceiling Wallboard Finishes | Ceiling | Finishes | Wallboard
D1010 Elevators & Lifts_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | D1010 | Elevators & Lifts | Elevators & Lifts | Elevators | Lifts |  | &
D1020 Escalators & Moving Walks_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | D1020 | Escalators & Moving walks | Escalators & Moving walks | Escalators | Moving walks |  | &
D1090 Other Conveying Systems_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Interior Structure | Unit | 0 | 0% | Green |  |  | D1090 | Other Conveying Systems | Other Conveying Systems | Other | Systems |  | Conveying
G2010 Roadways_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Parking/Traffic | Unit | 0 | 0% | Green |  |  | G2010 | Roadways | Roadways | Roadways
G2020 Parking Lots_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Parking/Traffic | Unit | 0 | 0% | Green |  |  | G2020 | Parking Lots | Parking Lots | Parking | Lots
G2030 Pedestrian Paving_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Parking/Traffic | Unit | 0 | 0% | Green |  |  | G2030 | Pedestrian Paving | Pedestrian Paving | Pedestrian | Paving
D2010 Plumbing Fixtures_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | D2010 | Plumbing Fixtures | Plumbing Fixtures | Plumbing | Fixtures
D2020 Domestic Water Distribution_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | SF | 0 | 0% | Green |  |  | D2020 | Domestic Distribution Water | Domestic Distribution Water | Domestic | Water |  | Distribution
D2030 Sanitary Waste_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | SF | 0 | 0% | Green |  |  | D2030 | Sanitary Waste | Sanitary Waste | Sanitary | Waste
D2040 Rain Water Drainage_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | SF | 0 | 0% | Green |  |  | D2040 | Rain Drainage Water | Rain Drainage Water | Rain | Water |  | Drainage
D4010 Sprinklers_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Safety/Security | SF | 0 | 0% | Green |  |  | D4010 | Sprinklers | Sprinklers | Sprinklers
D4020 Standpipes_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Safety/Security | SF | 0 | 0% | Green |  |  | D4020 | Standpipes | Standpipes | Standpipes
G3010 Water Supply_Domestic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3010 | Water Domestic Supply | Water Domestic Supply | Water | Supply | Domestic
G3010 Water Supply_Fire | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3010 | Water Fire Supply | Water Fire Supply | Water | Supply | Fire
B1020 Roof Construction_Concrete | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B1020 | Roof Concrete Construction | Roof Concrete Construction | Roof | Construction | Concrete
B1020 Roof Construction_Steel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B1020 | Roof Steel Construction | Roof Steel Construction | Roof | Construction | Steel
B3010 Roof Coverings_Asphalt Shingle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Shingle Asphalt Coverings | Roof Shingle Asphalt Coverings | Roof | Coverings | Asphalt | Shingle
B3010 Roof Coverings_Built-Up | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Built-Up Coverings | Roof Built-Up Coverings | Roof | Coverings | Built-Up
B3010 Roof Coverings_Concrete Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Tile Concrete Coverings | Roof Tile Concrete Coverings | Roof | Coverings | Concrete | Tile
B3010 Roof Coverings_Gravel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Gravel Coverings | Roof Gravel Coverings | Roof | Coverings | Gravel
B3010 Roof Coverings_Metal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Metal Coverings | Roof Metal Coverings | Roof | Coverings | Metal
B3010 Roof Coverings_Modified Bitumen | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Bitumen Modified Coverings | Roof Bitumen Modified Coverings | Roof | Coverings | Modified | Bitumen
B3010 Roof Coverings_Single Ply | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Ply Single Coverings | Roof Ply Single Coverings | Roof | Coverings | Single | Ply
B3010 Roof Coverings_Spanish Tile | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3010 | Roof Tile Spanish Coverings | Roof Tile Spanish Coverings | Roof | Coverings | Spanish | Tile
B3020 Roof Openings_Access Hatch | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | Unit | 0 | 0% | Green |  |  | B3020 | Roof Hatch Access Openings | Roof Hatch Access Openings | Roof | Openings | Access | Hatch
B3020 Roof Openings_Skylights | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Roofing | SF | 0 | 0% | Green |  |  | B3020 | Roof Skylights Openings | Roof Skylights Openings | Roof | Openings | Skylights
D4030 Fire Protection Specialties_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Safety/Security | SF | 0 | 0% | Green |  |  | D4030 | Fire Protection | Fire Protection | Fire | Protection
D5030 Communications & Security_Access Control System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5030 | Communications Access Control System | Communications Access Control System | Communications |  |  | Access Control System |  |  | Access Control System
D5030 Communications & Security_Clock / Intercom System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5030 | Communications Clock / Intercom System | Communications Clock / Intercom System | Communications |  |  | Clock / Intercom System |  |  | Clock / Intercom System
D5030 Communications & Security_Closed Circuit Surveillance | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5030 | Communications Closed Circuit Surveillance | Communications Closed Circuit Surveillance | Communications |  |  | Closed Circuit Surveillance |  |  | Closed Circuit Surveillance
D5030 Communications & Security_Fire Alarm / Detection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Safety/Security | SF | 0 | 0% | Green |  |  | D5030 | Communications Fire Alarm / Detection | Communications Fire Alarm / Detection | Communications |  |  | Fire Alarm / Detection |  |  | Fire Alarm / Detection
D5030 Communications & Security_Intrusion Alarm System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5030 | Communications Intrusion Alarm System | Communications Intrusion Alarm System | Communications |  |  | Intrusion Alarm System |  |  | Intrusion Alarm System
D5030 Communications & Security_Lighting Control System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5030 | Communications Lighting Control System | Communications Lighting Control System | Communications |  |  | Lighting Control System |  |  | Lighting Control System
D5030 Communications & Security_Voice / Data System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | D5030 | Communications Voice / Data System | Communications Voice / Data System | Communications |  |  | Voice / Data System |  |  | Voice / Data System
G2040 Site Development_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Site | Unit | 0 | 0% | Green |  |  | G2040 | Site Development | Site Development | Site | Development
G2050 Landscaping_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Site | Unit | 0 | 0% | Green |  |  | G2050 | Landscaping | Landscaping | Landscaping
G3020 Sanitary Sewer_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3020 | Sanitary Sewer | Sanitary Sewer | Sanitary | Sewer
G3030 Storm Sewer_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3030 | Storm Sewer | Storm Sewer | Storm | Sewer
G3040 Heating Distribution_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3040 | Heating Distribution | Heating Distribution | Heating | Distribution
G3050 Cooling Distribution_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3050 | Cooling Distribution | Cooling Distribution | Cooling | Distribution
G3060 Fuel Distribution_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Plumbing | Unit | 0 | 0% | Green |  |  | G3060 | Fuel Distribution | Fuel Distribution | Fuel | Distribution
G4030 Site Communications & Security_blank | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | Electrical | SF | 0 | 0% | Green |  |  | G4030 | Site Security Communications | Site Security Communications | Site | Communications |  | Security

## SYST_LC
School Name | Level I | Level II | Level III | Type | LOOKUP KEY | System Category | Deficiency | Replacement Value | Sys CI | Yr 0 LC $ | Yrs 1-5 LC $ | Yrs 6-10 LC $ | YRs 11-15 LC $ | System Category | Deficiency | Replacement Value | Sys CI | Yr 0 LC $ | Yrs 1-5 LC $ | Yrs 6-10 LC $ | YRs 11-15 LC $
0 | B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Hollow Metal | B2030 Exterior Doors_Hollow Metal | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Overhead Metal Garage | B2030 Exterior Doors_Overhead Metal Garage | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Rollup Metal | B2030 Exterior Doors_Rollup Metal | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Storefront | B2030 Exterior Doors_Storefront | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Wood | B2030 Exterior Doors_Wood | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Hollow Metal | C1020 Interior Doors_Hollow Metal | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Foundation | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Overhead Metal Garage | C1020 Interior Doors_Overhead Metal Garage | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Rollup Metal | C1020 Interior Doors_Rollup Metal | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Storefront | C1020 Interior Doors_Storefront | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Wood | C1020 Interior Doors_Wood | Doors | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Parking/Traffic | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5010 Electrical Service & Distribution | 0 | D5010 Electrical Service & Distribution_blank | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5020 Lighting and Branch Wiring | 0 | D5020 Lighting and Branch Wiring_blank | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G40 Site Electrical Utilities | G4010 Electrical Distribution | Generator | G4010 Electrical Distribution_Generator | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Safety/Security | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G40 Site Electrical Utilities | G4010 Electrical Distribution | Service | G4010 Electrical Distribution_Service | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 | Site | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G40 Site Electrical Utilities | G4020 Site Lighting | 0 | G4020 Site Lighting_blank | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0 |  | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Concrete Formed / Tilt | B2010 Exterior Walls_Concrete Formed / Tilt | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/ Wood Siding | B2010 Exterior Walls_Framed w/ Wood Siding | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Masonry Veneer | B2010 Exterior Walls_Framed w/Masonry Veneer | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Metal Panel | B2010 Exterior Walls_Framed w/Metal Panel | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Stucco | B2010 Exterior Walls_Framed w/Stucco | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Masonry | B2010 Exterior Walls_Masonry | Exterior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Aluminum/Steel | B2020 Exterior Windows_Aluminum/Steel | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Clad | B2020 Exterior Windows_Clad | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Curtain Wall | B2020 Exterior Windows_Curtain Wall | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Wood | B2020 Exterior Windows_Wood | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | Interior Windows | Aluminum/Steel | Interior Windows_Aluminum/Steel | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | 1 | C10 Interior Construction | Interior Windows | Clad | Interior Windows_Clad | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | Interior Windows | Wood | Interior Windows_Wood | Exterior/Interior Windows | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B10 Superstructure | B1010 Floor Construction | Concrete | B1010 Floor Construction_Concrete | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B10 Superstructure | B1010 Floor Construction | Steel | B1010 Floor Construction_Steel | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B10 Superstructure | B1010 Floor Construction | Wood | B1010 Floor Construction_Wood | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B10 Superstructure | B1020 Roof Construction | Wood | B1020 Roof Construction_Wood | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Carpet / Soft Surface | C3020 Floor Finishes_Carpet / Soft Surface | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Ceramic Tile | C3020 Floor Finishes_Ceramic Tile | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Liquid Applied | C3020 Floor Finishes_Liquid Applied | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Polished Concrete | C3020 Floor Finishes_Polished Concrete | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Resilient Sheet | C3020 Floor Finishes_Resilient Sheet | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Resilient Tile | C3020 Floor Finishes_Resilient Tile | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Wood Sports Floor | C3020 Floor Finishes_Wood Sports Floor | Flooring | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | A SUBSTRUCTURE | A10 Foundations | A1010 Standard Foundations | 0 | A1010 Standard Foundations_blank | Foundation | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | A SUBSTRUCTURE | A10 Foundations | A1020 Special Foundations | 0 | A1020 Special Foundations_blank | Foundation | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | A SUBSTRUCTURE | A10 Foundations | A1030 Slab on Grade | 0 | A1030 Slab on Grade_blank | Foundation | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | A SUBSTRUCTURE | A10 Foundations | A2020 Basement Walls | 0 | A2020 Basement Walls_blank | Foundation | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E10 Equipment | E1010 Commercial Equipment | Food Service | E1010 Commercial Equipment_Food Service | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E10 Equipment | E1010 Commercial Equipment | Vocational | E1010 Commercial Equipment_Vocational | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Art | E1020 Institutional Equipment_Art | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Restroom Accessories/Stalls | E1020 Institutional Equipment_Restroom Accessories/Stalls | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Science | E1020 Institutional Equipment_Science | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Stage Performance | E1020 Institutional Equipment_Stage Performance | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E20 Furnishings | E2010 Fixed Furnishings | 0 | E2010 Fixed Furnishings_blank | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | E EQUIPMENT & FURNISHINGS | E20 Furnishings | E2020 Movable Furnishings | 0 | E2020 Movable Furnishings_blank | Furnishing, Fixtures, Equipment | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3010 Energy Supply | 0 | D3010 Energy Supply_blank | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Air Handler | D3020 Heat Generating Systems_Air Handler | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Boiler | D3020 Heat Generating Systems_Boiler | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Furnace | D3020 Heat Generating Systems_Furnace | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Heat Exchanger | D3020 Heat Generating Systems_Heat Exchanger | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3030 Cooling Generating Systems | Component of air handler | D3030 Cooling Generating Systems_Component of air handler | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3030 Cooling Generating Systems | Stand alone chiller | D3030 Cooling Generating Systems_Stand alone chiller | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3040 Distribution Systems | Ductwork | D3040 Distribution Systems_Ductwork | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3040 Distribution Systems | Hot water return & supply | D3040 Distribution Systems_Hot water return & supply | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3050 Terminal & Package Units | Above ceiling VAV unit | D3050 Terminal & Package Units_Above ceiling VAV unit | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3050 Terminal & Package Units | In-room radiant unit | D3050 Terminal & Package Units_In-room radiant unit | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3050 Terminal & Package Units | In-room ventilator unit | D3050 Terminal & Package Units_In-room ventilator unit | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3060 Controls & Instrumentation | 0 | D3060 Controls & Instrumentation_blank | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D30 HVAC | D3070 Systems Testing & Balancing | 0 | D3070 Systems Testing & Balancing_blank | HVAC | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1010 Partitions | Curtain Wall | C1010 Partitions_Curtain Wall | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1010 Partitions | Framed | C1010 Partitions_Framed | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C10 Interior Construction | C1010 Partitions | Masonry | C1010 Partitions_Masonry | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2010 Stair Construction | Concrete | C2010 Stair Construction_Concrete | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2010 Stair Construction | Metal | C2010 Stair Construction_Metal | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2010 Stair Construction | Wood | C2010 Stair Construction_Wood | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2020 Stair Finishes | Concrete Fill | C2020 Stair Finishes_Concrete Fill | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2020 Stair Finishes | Metal Grating | C2020 Stair Finishes_Metal Grating | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2020 Stair Finishes | Resilient | C2020 Stair Finishes_Resilient | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C20 Stairs | C2020 Stair Finishes | Wood | C2020 Stair Finishes_Wood | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Ceramic Tile | C3010 Wall Finishes_Ceramic Tile | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Formica | C3010 Wall Finishes_Formica | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Paint on Masonry | C3010 Wall Finishes_Paint on Masonry | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Vinyl Paneling | C3010 Wall Finishes_Vinyl Paneling | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wainscot | C3010 Wall Finishes_Wainscot | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wallboard | C3010 Wall Finishes_Wallboard | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wood Paneling | C3010 Wall Finishes_Wood Paneling | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Glued-Up Ceiling Tile | C3030 Ceiling Finishes_Glued-Up Ceiling Tile | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Lay-In Ceiling Tile | C3030 Ceiling Finishes_Lay-In Ceiling Tile | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Painted Structure | C3030 Ceiling Finishes_Painted Structure | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Tectum | C3030 Ceiling Finishes_Tectum | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Wallboard | C3030 Ceiling Finishes_Wallboard | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D10 Conveying | D1010 Elevators & Lifts | 0 | D1010 Elevators & Lifts_blank | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D10 Conveying | D1020 Escalators & Moving Walks | 0 | D1020 Escalators & Moving Walks_blank | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D10 Conveying | D1090 Other Conveying Systems | 0 | D1090 Other Conveying Systems_blank | Interior Structure | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G20 Site Improvements | G2010 Roadways | 0 | G2010 Roadways_blank | Parking/Traffic | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G20 Site Improvements | G2020 Parking Lots | 0 | G2020 Parking Lots_blank | Parking/Traffic | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G20 Site Improvements | G2030 Pedestrian Paving | 0 | G2030 Pedestrian Paving_blank | Parking/Traffic | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D20 Plumbing | D2010 Plumbing Fixtures | 0 | D2010 Plumbing Fixtures_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D20 Plumbing | D2020 Domestic Water Distribution | 0 | D2020 Domestic Water Distribution_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D20 Plumbing | D2030 Sanitary Waste | 0 | D2030 Sanitary Waste_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D20 Plumbing | D2040 Rain Water Drainage | 0 | D2040 Rain Water Drainage_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D40 Fire Protection | D4010 Sprinklers | 0 | D4010 Sprinklers_blank | Safety/Security | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D40 Fire Protection | D4020 Standpipes | 0 | D4020 Standpipes_blank | Safety/Security | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3010 Water Supply | Domestic | G3010 Water Supply_Domestic | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3010 Water Supply | Fire | G3010 Water Supply_Fire | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B10 Superstructure | B1020 Roof Construction | Concrete | B1020 Roof Construction_Concrete | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B10 Superstructure | B1020 Roof Construction | Steel | B1020 Roof Construction_Steel | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Asphalt Shingle | B3010 Roof Coverings_Asphalt Shingle | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Built-Up | B3010 Roof Coverings_Built-Up | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Concrete Tile | B3010 Roof Coverings_Concrete Tile | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Gravel | B3010 Roof Coverings_Gravel | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Metal | B3010 Roof Coverings_Metal | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Modified Bitumen | B3010 Roof Coverings_Modified Bitumen | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Single Ply | B3010 Roof Coverings_Single Ply | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3010 Roof Coverings | Spanish Tile | B3010 Roof Coverings_Spanish Tile | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3020 Roof Openings | Access Hatch | B3020 Roof Openings_Access Hatch | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | B SHELL | B30 Roofing | B3020 Roof Openings | Skylights | B3020 Roof Openings_Skylights | Roofing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D40 Fire Protection | D4030 Fire Protection Specialties | 0 | D4030 Fire Protection Specialties_blank | Safety/Security | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Access Control System | D5030 Communications & Security_Access Control System | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Clock / Intercom System | D5030 Communications & Security_Clock / Intercom System | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Closed Circuit Surveillance | D5030 Communications & Security_Closed Circuit Surveillance | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Fire Alarm / Detection | D5030 Communications & Security_Fire Alarm / Detection | Safety/Security | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Intrusion Alarm System | D5030 Communications & Security_Intrusion Alarm System | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Lighting Control System | D5030 Communications & Security_Lighting Control System | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | D SERVICES | D50 Electrical | D5030 Communications & Security | Voice / Data System | D5030 Communications & Security_Voice / Data System | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G20 Site Improvements | G2040 Site Development | 0 | G2040 Site Development_blank | Site | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G20 Site Improvements | G2050 Landscaping | 0 | G2050 Landscaping_blank | Site | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3020 Sanitary Sewer | 0 | G3020 Sanitary Sewer_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3030 Storm Sewer | 0 | G3030 Storm Sewer_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3040 Heating Distribution | 0 | G3040 Heating Distribution_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3050 Cooling Distribution | 0 | G3050 Cooling Distribution_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3060 Fuel Distribution | 0 | G3060 Fuel Distribution_blank | Plumbing | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0
0 | G BUILDING SITE WORK | G40 Site Electrical Utilities | G4030 Site Communications & Security | 0 | G4030 Site Communications & Security_blank | Electrical | 0 | 0 | #DIV/0! | 0 | 0 | 0 | 0

## AUTO_NOTES
| Category | Def. Category | # | % Sys by Def. Category | $ Repair | $ Replace | %Major/Replace | % SYS CI <HIDE> | %Major/Replace | % SYS CI | R/Y/G | Auto Generated Notes | DRAFT NOTES IF NO MAJOR/REPLACE <HIDE> | Major/Replacements (clean text) <HIDE> | Minor/Moderate (clean text) <HIDE> | Concatenated notes (raw) | Notes for Manual Entry
| Doors | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0 0 0
| Doors | Minor | 0 | #DIV/0! | 0 | 0
| Doors | Moderate | 0 | #DIV/0! | 0 | 0
| Doors | Major | 0 | #DIV/0! | 0 | 0
| Doors | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Doors | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Electrical | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0 0 0 0 0
| Electrical | Minor | 0 | #DIV/0! | 0 | 0
| Electrical | Moderate | 0 | #DIV/0! | 0 | 0
| Electrical | Major | 0 | #DIV/0! | 0 | 0
| Electrical | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Electrical | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Exterior Structure | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0
| Exterior Structure | Minor | 0 | #DIV/0! | 0 | 0
| Exterior Structure | Moderate | 0 | #DIV/0! | 0 | 0
| Exterior Structure | Major | 0 | #DIV/0! | 0 | 0
| Exterior Structure | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Exterior Structure | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Exterior/Interior Windows | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0
| Exterior/Interior Windows | Minor | 0 | #DIV/0! | 0 | 0
| Exterior/Interior Windows | Moderate | 0 | #DIV/0! | 0 | 0
| Exterior/Interior Windows | Major | 0 | #DIV/0! | 0 | 0
| Exterior/Interior Windows | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Exterior/Interior Windows | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Flooring | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0
| Flooring | Minor | 0 | #DIV/0! | 0 | 0
| 1 | Moderate | Insert an estimated local cost inflation factor based on how much local costs are greater/lesser than the base prices in the PCA Cost Tables. (E.g., 1.15 = costs are ~ 15% greater than the average in the PCA Cost Table. If costs are considered average, keep the value "1") | #VALUE! | 0 | 0
| 1 | Major | 0 | #DIV/0! | 0 | 0
| 1 | Replace as part of Renovation | Name of the company performing the assessment | #VALUE! | 0 | 0
Initial Assessor Name: | 1 | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Foundation | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0
| Foundation | Minor | 0 | #DIV/0! | 0 | 0
| Foundation | Moderate | 0 | #DIV/0! | 0 | 0
| Foundation | Major | 0 | #DIV/0! | 0 | 0
| Foundation | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Foundation | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Furnishing, Fixtures, Equipment | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0
| Furnishing, Fixtures, Equipment | Minor | 0 | #DIV/0! | 0 | 0
| Furnishing, Fixtures, Equipment | Moderate | 0 | #DIV/0! | 0 | 0
| Furnishing, Fixtures, Equipment | Major | 0 | #DIV/0! | 0 | 0
| Furnishing, Fixtures, Equipment | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Furnishing, Fixtures, Equipment | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| HVAC | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0 0 0 0 0 0 0
| HVAC | Minor | 0 | #DIV/0! | 0 | 0
| HVAC | Moderate | 0 | #DIV/0! | 0 | 0
| HVAC | Major | 0 | #DIV/0! | 0 | 0
| HVAC | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| HVAC | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Interior Structure | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0
| Interior Structure | Minor | 0 | #DIV/0! | 0 | 0
| Interior Structure | Moderate | 0 | #DIV/0! | 0 | 0
| Interior Structure | Major | 0 | #DIV/0! | 0 | 0
| Interior Structure | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Interior Structure | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Parking/Traffic | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0
| Parking/Traffic | Minor | 0 | #DIV/0! | 0 | 0
| Parking/Traffic | Moderate | 0 | #DIV/0! | 0 | 0
| Parking/Traffic | Major | 0 | #DIV/0! | 0 | 0
| Parking/Traffic | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Parking/Traffic | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Plumbing | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0 0 0 0
| Plumbing | Minor | 0 | #DIV/0! | 0 | 0
| Plumbing | Moderate | 0 | #DIV/0! | 0 | 0
| Plumbing | Major | 0 | #DIV/0! | 0 | 0
| Plumbing | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Plumbing | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Roofing | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0 0 0 0 0 0 0 0 0 0
| Roofing | Minor | 0 | #DIV/0! | 0 | 0
| Roofing | Moderate | 0 | #DIV/0! | 0 | 0
| Roofing | Major | 0 | #DIV/0! | 0 | 0
| Roofing | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Roofing | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Safety/Security | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0 0 0
| Safety/Security | Minor | 0 | #DIV/0! | 0 | 0
| Safety/Security | Moderate | 0 | #DIV/0! | 0 | 0
| Safety/Security | Major | 0 | #DIV/0! | 0 | 0
| Safety/Security | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Safety/Security | Replace as singular scope | 0 | #DIV/0! | 0 | 0
| Site | None | 0 | #DIV/0! | 0 | 0 | 0 | #DIV/0! | None | <1% | Green | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. |  |  | 0 0
| Site | Minor | 0 | #DIV/0! | 0 | 0
| Site | Moderate | 0 | #DIV/0! | 0 | 0
| Site | Major | 0 | #DIV/0! | 0 | 0
| Site | Replace as part of Renovation | 0 | #DIV/0! | 0 | 0
| Site | Replace as singular scope | 0 | #DIV/0! | 0 | 0

## PCA Cost Tables - READ ONLY
District Name: |  | 0
Site Name: |  | 0 |  |  | Costs by level of action and system should be carefully reviewed and modified to reflect local current cost estimates.
Building Name: |  | 0
Building ID: |  | 0
LEVEL OF ACTION
Level 1 | Level 2 | Level 3 | Type (as applicable) | Lookup Key |  | Minor |  | Moderate |  | Major |  | Replace as part of Renovation |  | Replace as singular scope | Forwarded Unit Budget | Cost Estimator Notes
A SUBSTRUCTURE
A SUBSTRUCTURE | A10 Foundations
A SUBSTRUCTURE | A10 Foundations | A1010 Standard Foundations | blank | A1010 Standard Foundations_blank | 0.6549 |  | 13.098 |  | 36.2553 |  | 0 | Replace |  | Replace | 0
A SUBSTRUCTURE | A10 Foundations | A1020 Special Foundations | blank | A1020 Special Foundations_blank | 0.6549 |  | 19.647 |  | 46.2097 |  | 0 | Replace |  | Replace | 0
A SUBSTRUCTURE | A10 Foundations | A1030 Slab on Grade | blank | A1030 Slab on Grade_blank | 2.7899 |  | 12.4431 |  | 34.7097 |  | 0 | Replace |  | Replace | 0
A SUBSTRUCTURE | A20 Basement Construction | A1030 Slab on Grade | blank | A1030 Slab on Grade_blank
A SUBSTRUCTURE | A20 Basement Construction | A2010 Basement Excavation | blank | A2010 Basement Excavation_blank | [7 empty] | Replace |  | Replace | 0
A SUBSTRUCTURE | A20 Basement Construction | A2020 Basement Walls | blank | A2020 Basement Walls_blank | 0.87757 |  | 2.7899 |  | 11.7358 |  | 0 | Replace |  | Replace | 0
B SHELL
B SHELL | B10 Superstructure | B1010 Floor Construction | Wood | B1010 Floor Construction_Wood | 5.3625 |  | 12.012 |  | 76.8625 |  | 201.9875 | Replace | 113 | Replace | 0
B SHELL | B10 Superstructure | B1010 Floor Construction | Steel | B1010 Floor Construction_Steel | 7.7935 |  | 15.3153 |  | 81.3241 |  | 202.4451 | Replace | 117 | Replace | 0
B SHELL | B10 Superstructure | B1010 Floor Construction | Concrete | B1010 Floor Construction_Concrete | 9.1686 |  | 18.3372 |  | 69.4194 |  | 161.1054 | Replace | 123 | Replace | 0
B SHELL | B10 Superstructure | B1020 Roof Construction | Wood | B1020 Roof Construction_Wood | 5.8094 |  | 13.6207 |  | 58.9875 |  | 157.3 | Replace | 88 | Replace | 0
B SHELL | B10 Superstructure | B1020 Roof Construction | Steel | B1020 Roof Construction_Steel | 8.4549 |  | 16.8204 |  | 66.1375 |  | 164.45 | Replace | 92 | Replace | 0
B SHELL | B10 Superstructure | B1020 Roof Construction | Concrete | B1020 Roof Construction_Concrete | 9.8497 |  | 20.5377 |  | 56.3214 |  | 129.6702 | Replace | 99 | Replace | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Concrete Formed / Tilt | B2010 Exterior Walls_Concrete Formed / Tilt | 4.2569 |  | 6.1561 |  | 26.196 |  | 0 | Replace |  | Replace | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Masonry | B2010 Exterior Walls_Masonry | 4.2569 |  | 8.8019 |  | 27.663 |  | 42.8698 | Replace | 37.73 | Replace | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/ Wood Siding | B2010 Exterior Walls_Framed w/ Wood Siding | 5.4876 |  | 10.4032 |  | 33.0688 |  | 45.5991 | Replace | 30.51 | Replace | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Metal Panel | B2010 Exterior Walls_Framed w/Metal Panel | 6.3814 |  | 12.1907 |  | 34.32 |  | 54.5366 | Replace | 35.51 | Replace | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Stucco | B2010 Exterior Walls_Framed w/Stucco | 4.0211 |  | 7.623 |  | 26.196 |  | 40.1978 | Replace | 35.69 | Replace | 0
B SHELL | B20 Exterior Enclosure | B2010 Exterior Walls | Framed w/Masonry Veneer | B2010 Exterior Walls_Framed w/Masonry Veneer | 3.2221 |  | 5.8679 |  | 32.0901 |  | 50.5714 | Replace | 43.61 | Replace | 0
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Wood | B2020 Exterior Windows_Wood | 89.375 |  | 357.5 |  | 893.75 |  | 1787.5 | Replace | 1000 | Replace | 0 | Per Window
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Aluminum/Steel | B2020 Exterior Windows_Aluminum/Steel | 31.5 |  | 126 |  | 1102.5 |  | 2205 | Replace | 1400 | Replace | 0 | Per Window
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Clad | B2020 Exterior Windows_Clad | 119.07 |  | 476.28 |  | 1587.6 |  | 3175.2 | Replace | 2000 | Replace | 0 | Per Window
B SHELL | B20 Exterior Enclosure | B2020 Exterior Windows | Curtain Wall | B2020 Exterior Windows_Curtain Wall | 39.69 |  | 158.76 |  | 1190.7 |  | 2381.4 | Replace | 30 | Replace | 0 | Per Window
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Wood | B2030 Exterior Doors_Wood | 446.875 |  | 1787.5 |  | 2681.25 |  | 3575 | Replace | 2000 | Replace | 0 | Per leaf
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Hollow Metal | B2030 Exterior Doors_Hollow Metal | 446.875 |  | 1787.5 |  | 2323.75 |  | 3217.5 | Replace | 1800 | Replace | 0 | Per leaf
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Storefront | B2030 Exterior Doors_Storefront | 450.45 |  | 2162.16 |  | 4324.32 |  | 5405.4 | Replace | 3000 | Replace | 0 | Per leaf
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Overhead Metal Garage | B2030 Exterior Doors_Overhead Metal Garage | 268.125 |  | 536.25 |  | 1072.5 |  | 2681.25 | Replace | 1500 | Replace | 0 | Per Single bay
B SHELL | B20 Exterior Enclosure | B2030 Exterior Doors | Rollup Metal | B2030 Exterior Doors_Rollup Metal | 178.75 |  | 446.875 |  | 893.75 |  | 1787.5 | Replace | 1000 | Replace | 0 | Per Single bay
B SHELL | B30 Roofing | B3010 Roof Coverings | Asphalt Shingle | B3010 Roof Coverings_Asphalt Shingle | 2.3058 |  | 6.5075 |  | 18.361 |  | 25.62 | Replace | 15 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Modified Bitumen | B3010 Roof Coverings_Modified Bitumen | 2.3058 |  | 6.5075 |  | 18.361 |  | 25.62 | Replace | 16 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Gravel | B3010 Roof Coverings_Gravel | 2.6816 |  | 6.7978 |  | 20.0861 |  | 44.408 | Replace | 17 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Spanish Tile | B3010 Roof Coverings_Spanish Tile | 3.885 |  | 9.1375 |  | 25.2525 |  | 52.836 | Replace | 34 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Built-Up | B3010 Roof Coverings_Built-Up | 2.6816 |  | 6.7978 |  | 20.0861 |  | 44.408 | Replace | 26 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Single Ply | B3010 Roof Coverings_Single Ply | 4.0138 |  | 7.2761 |  | 19.3175 |  | 40.992 | Replace | 24 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Metal | B3010 Roof Coverings_Metal | 4.29 |  | 9.6167 |  | 25.025 |  | 57.2 | Replace | 32 | Replace | 0
B SHELL | B30 Roofing | B3010 Roof Coverings | Concrete Tile | B3010 Roof Coverings_Concrete Tile | 3.885 |  | 9.1375 |  | 25.2525 |  | 52.836 | Replace | 34 | Replace | 0
B SHELL | B30 Roofing | B3020 Roof Openings | Skylights | B3020 Roof Openings_Skylights | 0.13986 |  | 0.41958 |  | 1.3986 |  | 2.7972 | Replace | 4.78 | Replace | 0 | By Building GFA
B SHELL | B30 Roofing | B3020 Roof Openings | Access Hatch | B3020 Roof Openings_Access Hatch | 368.75 |  | 737.5 |  | 2212.5 |  | 5162.5 | Replace | 0.33 | Replace | 0 | Per hatch
C INTERIORS
C INTERIORS | C10 Interior Construction | C1010 Partitions | Framed | C1010 Partitions_Framed | 3.9683 |  | 11.9048 |  | 19.8413 |  | 24.8889 | Replace | 50.68 | Replace | 0
C INTERIORS | C10 Interior Construction | C1010 Partitions | Masonry | C1010 Partitions_Masonry | 6.811 |  | 12.4431 |  | 23.9038 |  | 38.22 | Replace | 64.18 | Replace | 0
C INTERIORS | C10 Interior Construction | C1010 Partitions | Curtain Wall | C1010 Partitions_Curtain Wall | 3.843 |  | 15.372 |  | 76.86 |  | 384.3 | Replace | 250 | Replace | 0
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Wood | C1020 Interior Doors_Wood | 446.875 |  | 1430 |  | 2323.75 |  | 3217.5 | Replace | 1800 | Replace | 0 | Per leaf
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Hollow Metal | C1020 Interior Doors_Hollow Metal | 446.875 |  | 1430 |  | 1966.25 |  | 2860 | Replace | 1600 | Replace | 0 | Per leaf
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Storefront | C1020 Interior Doors_Storefront | 450.45 |  | 2162.16 |  | 4324.32 |  | 5405.4 | Replace | 3000 | Replace | 0 | Per Unit
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Overhead Metal Garage | C1020 Interior Doors_Overhead Metal Garage | 268.125 |  | 536.25 |  | 1072.5 |  | 2681.25 | Replace | 1500 | Replace | 0 | Per Single bay
C INTERIORS | C10 Interior Construction | C1020 Interior Doors | Rollup Metal | C1020 Interior Doors_Rollup Metal | 178.75 |  | 446.875 |  | 893.75 |  | 1787.5 | Replace | 1000 | Replace | 0 | Per Single bay
C INTERIORS | C10 Interior Construction | Interior Windows | Wood | Interior Windows_Wood | 89.375 |  | 357.5 |  | 893.75 |  | 1787.5 | Replace | 1000 | Replace | 0 | Per Window
C INTERIORS | C10 Interior Construction | Interior Windows | Aluminum/Steel | Interior Windows_Aluminum/Steel | 31.5 |  | 126 |  | 1102.5 |  | 2205 | Replace | 1400 | Replace | 0 | Per Window
C INTERIORS | C10 Interior Construction | Interior Windows | Clad | Interior Windows_Clad | 115.29 |  | 461.16 |  | 1537.2 |  | 3074.4 | Replace | 2000 | Replace | 0 | Per Window
C INTERIORS | C20 Stairs | C2010 Stair Construction | Wood | C2010 Stair Construction_Wood | 893.75 |  | 8937.5 |  | 19662.5 |  | 44687.5 | Replace | 2.34 | Replace | 0 | Cost/Flight
C INTERIORS | C20 Stairs | C2010 Stair Construction | Metal | C2010 Stair Construction_Metal | 1340.625 |  | 8937.5 |  | 26812.5 |  | 53625 | Replace | 2.4 | Replace | 0 | Cost/Flight
C INTERIORS | C20 Stairs | C2010 Stair Construction | Concrete | C2010 Stair Construction_Concrete | 885 |  | 8850 |  | 23600 |  | 41300 | Replace | 4.92 | Replace | 0 | Cost/Flight
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Concrete Fill | C2020 Stair Finishes_Concrete Fill | 982.35 |  | 1964.7 |  | 3929.4 |  | 6549 | Replace | 1.96 | Replace | 0 | Cost/Flight
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Resilient | C2020 Stair Finishes_Resilient | 654.9 |  | 982.35 |  | 1964.7 |  | 3274.5 | Replace | 1.5 | Replace | 0 | Cost/Flight
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Wood | C2020 Stair Finishes_Wood | 793.65 |  | 1587.3 |  | 2380.95 |  | 3968.25 | Replace | 1.5 | Replace | 0 | Cost/Flight
C INTERIORS | C20 Stairs | C2020 Stair Finishes | Metal Grating | C2020 Stair Finishes_Metal Grating | 952.38 |  | 1904.76 |  | 3174.6 |  | 4761.9 | Replace | 1.5 | Replace | 0 | Cost/Flight
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Paint on Masonry | C3010 Wall Finishes_Paint on Masonry | 2.934 |  | 4.1914 |  | 5.1082 |  | 5.7238 | Replace | 5.37 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wallboard | C3010 Wall Finishes_Wallboard | 2.6458 |  | 3.2221 |  | 6.8765 |  | 10.557 | Replace | 9.06 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wainscot | C3010 Wall Finishes_Wainscot | 2.6458 |  | 3.5365 |  | 7.0729 |  | 11.1333 | Replace | 8.5 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Wood Paneling | C3010 Wall Finishes_Wood Paneling | 3.2063 |  | 11.9048 |  | 15.873 |  | 23.8095 | Replace | 15 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Vinyl Paneling | C3010 Wall Finishes_Vinyl Paneling | 2.6458 |  | 9.627 |  | 12.7706 |  | 15.7176 | Replace | 12 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Formica | C3010 Wall Finishes_Formica | 3.4965 |  | 10.8392 |  | 13.986 |  | 20.979 | Replace | 15 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3010 Wall Finishes | Ceramic Tile | C3010 Wall Finishes_Ceramic Tile | 1.1788 |  | 1.5718 |  | 2.6196 |  | 3.1828 | Replace | 3.43 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Carpet / Soft Surface | C3020 Floor Finishes_Carpet / Soft Surface | 0.39294 |  | 5.2392 |  | 8.7495 |  | 11.3691 | Replace | 8.68 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Resilient Tile | C3020 Floor Finishes_Resilient Tile | 1.3229 |  | 2.947 |  | 6.2346 |  | 8.9066 | Replace | 8.8 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Resilient Sheet | C3020 Floor Finishes_Resilient Sheet | 2.6458 |  | 7.8588 |  | 15.7176 |  | 18.3372 | Replace | 14 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Polished Concrete | C3020 Floor Finishes_Polished Concrete | 2.6458 |  | 6.2216 |  | 11.7882 |  | 14.4078 | Replace | 11 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Ceramic Tile | C3020 Floor Finishes_Ceramic Tile | 4.9903 |  | 15.7176 |  | 32.9284 |  | 35.548 | Replace | 27.14 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Liquid Applied | C3020 Floor Finishes_Liquid Applied | 5.2392 |  | 10.3343 |  | 18.4813 |  | 21.1009 | Replace | 16.11 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3020 Floor Finishes | Wood Sports Floor | C3020 Floor Finishes_Wood Sports Floor | 8.9375 |  | 12.5125 |  | 32.175 |  | 35.75 | Replace | 20 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Wallboard | C3030 Ceiling Finishes_Wallboard | 4.1128 |  | 9.1686 |  | 11.7882 |  | 15.7176 | Replace | 14 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Lay-In Ceiling Tile | C3030 Ceiling Finishes_Lay-In Ceiling Tile | 1.3098 |  | 1.8206 |  | 5.2392 |  | 10.4784 | Replace | 10 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Glued-Up Ceiling Tile | C3030 Ceiling Finishes_Glued-Up Ceiling Tile | 0.85137 |  | 1.3098 |  | 3.2745 |  | 6.2085 | Replace | 6.74 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Tectum | C3030 Ceiling Finishes_Tectum | 0.85137 |  | 1.3098 |  | 3.2745 |  | 6.2085 | Replace | 5 | Replace | 0
C INTERIORS | C30 Interior Finishes | C3030 Ceiling Finishes | Painted Structure | C3030 Ceiling Finishes_Painted Structure | 0.52392 |  | 0.98235 |  | 2.6196 |  | 4.2045 | Replace | 5.21 | Replace | 0
D SERVICES
D SERVICES | D10 Conveying | D1010 Elevators & Lifts | blank | D1010 Elevators & Lifts_blank | 7789.272 |  | 12520.704 |  | 23476.32 |  | 84514.752 | Replace | 60000 | Replace | 0
D SERVICES | D10 Conveying | D1020 Escalators & Moving Walks | blank | D1020 Escalators & Moving Walks_blank | 5322.45 |  | 15835.008 |  | 156692.928 |  | 172137.76 | Replace | 120000 | Replace | 0
D SERVICES | D10 Conveying | D1090 Other Conveying Systems | blank | D1090 Other Conveying Systems_blank | 1520.7 |  | 6260.352 |  | 38017.5 |  | 41100 | Replace | 30000 | Replace | 0
D SERVICES | D20 Plumbing | D2010 Plumbing Fixtures | blank | D2010 Plumbing Fixtures_blank | 130.98 |  | 654.9 |  | 1964.7 |  | 3929.4 | Replace | 3000 | Replace | 0 | Price per unit
D SERVICES | D20 Plumbing | D2020 Domestic Water Distribution | blank | D2020 Domestic Water Distribution_blank | 1.6111 |  | 2.2005 |  | 9.5353 |  | 15.7176 | Replace | 77.38 | Replace | 0
D SERVICES | D20 Plumbing | D2030 Sanitary Waste | blank | D2030 Sanitary Waste_blank | 0.6549 |  | 2.0564 |  | 2.4231 |  | 2.7113 | Replace | 72.07 | Replace | 0
D SERVICES | D20 Plumbing | D2040 Rain Water Drainage | blank | D2040 Rain Water Drainage_blank | 0.39294 |  | 1.3229 |  | 2.4231 |  | 3.078 | Replace | 72.35 | Replace | 0
D SERVICES | D20 Plumbing | D2090 Other Plumbing Systems | blank | D2090 Other Plumbing Systems_blank | [7 empty] | Replace |  | Replace | 0
D SERVICES | D30 HVAC | D2090 Other Plumbing Systems | blank | D2090 Other Plumbing Systems_blank
D SERVICES | D30 HVAC | D3010 Energy Supply | blank | D3010 Energy Supply_blank | 1.8978 |  | 4.2275 |  | 11.186 |  | 19.6565 | Replace | 12.74 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Boiler | D3020 Heat Generating Systems_Boiler | 3.3974 |  | 4.3393 |  | 8.6618 |  | 16.0117 | Replace | 9.52 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Air Handler | D3020 Heat Generating Systems_Air Handler | 1.2614 |  | 3.1956 |  | 4.0534 |  | 9.7887 | Replace | 5.82 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Furnace | D3020 Heat Generating Systems_Furnace | 1.2446 |  | 2.2537 |  | 4.1375 |  | 7.1649 | Replace | 4.26 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3020 Heat Generating Systems | Heat Exchanger | D3020 Heat Generating Systems_Heat Exchanger | 0.33638 |  | 0.94186 |  | 1.6987 |  | 3.3974 | Replace | 2.02 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3030 Cooling Generating Systems | Component of air handler | D3030 Cooling Generating Systems_Component of air handler | 0.84095 |  | 2.0687 |  | 4.0534 |  | 6.4921 | Replace | 3.86 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3030 Cooling Generating Systems | Stand alone chiller | D3030 Cooling Generating Systems_Stand alone chiller | 1.2614 |  | 3.1956 |  | 4.0534 |  | 9.3177 | Replace | 5.54 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3040 Distribution Systems | Ductwork | D3040 Distribution Systems_Ductwork | 0.84095 |  | 3.0106 |  | 3.5824 |  | 8.6618 | Replace | 35.15 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3040 Distribution Systems | Hot water return & supply | D3040 Distribution Systems_Hot water return & supply | 2.0687 |  | 2.8256 |  | 7.5686 |  | 14.4139 | Replace | 35.15 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3050 Terminal & Package Units | Above ceiling VAV unit | D3050 Terminal & Package Units_Above ceiling VAV unit | 2.0687 |  | 4.0534 |  | 6.7781 |  | 13.0347 | Replace | 16.03 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3050 Terminal & Package Units | In-room ventilator unit | D3050 Terminal & Package Units_In-room ventilator unit | 3.3638 |  | 9.0486 |  | 20.1828 |  | 26.8431 | Replace | 27.96 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3050 Terminal & Package Units | In-room radiant unit | D3050 Terminal & Package Units_In-room radiant unit | 0.84095 |  | 1.8837 |  | 4.0534 |  | 5.2812 | Replace | 15.14 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3060 Controls & Instrumentation | blank | D3060 Controls & Instrumentation_blank | 0.94186 |  | 1.5137 |  | 4.5243 |  | 8.6113 | Replace | 14.69 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3070 Systems Testing & Balancing | blank | D3070 Systems Testing & Balancing_blank | 0 |  | 0 |  | 0 |  | 2.0846 | Replace | 1.46 | Replace | 0 | Cost/SF of building GFA
D SERVICES | D30 HVAC | D3090 Other HVAC Systems & Equipment | NOT USED | D3090 Other HVAC Systems & Equipment_NOT USED | [7 empty] | Replace |  | Replace | 0
D SERVICES | D40 Fire Protection | D4010 Sprinklers | blank | D4010 Sprinklers_blank | 1.5583 |  | 5.6162 |  | 14.2718 |  | 28.7597 | Replace | 18.64 | Replace | 0
D SERVICES | D40 Fire Protection | D4020 Standpipes | blank | D4020 Standpipes_blank | 2.1292 |  | 3.4561 |  | 8.8717 |  | 15.7993 | Replace | 10.24 | Replace | 0
D SERVICES | D40 Fire Protection | D4030 Fire Protection Specialties | blank | D4030 Fire Protection Specialties_blank | 11.5393 |  | 11.5393 |  | 43.4199 |  | 63.0669 | Replace | 48.15 | Replace | 0
D SERVICES | D40 Fire Protection | D4090 Other Fire Protection Systems | blank | D4090 Other Fire Protection Systems_blank | [7 empty] | Replace |  | Replace | 0
D SERVICES | D50 Electrical | D5010 Electrical Service & Distribution | blank | D5010 Electrical Service & Distribution_blank | 1.9119 |  | 5.5648 |  | 9.7461 |  | 12.6062 | Replace | 18.11 | Replace | 0
D SERVICES | D50 Electrical | D5020 Lighting and Branch Wiring | blank | D5020 Lighting and Branch Wiring_blank | 1.9119 |  | 6.2176 |  | 8.5337 |  | 27.9792 | Replace | 37.95 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Voice / Data System | D5030 Communications & Security_Voice / Data System | 0.31088 |  | 1.9119 |  | 5.658 |  | 18.6528 | Replace | 18.64 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Clock / Intercom System | D5030 Communications & Security_Clock / Intercom System | 0.15544 |  | 0.43523 |  | 1.5544 |  | 3.1088 | Replace | 2 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Closed Circuit Surveillance | D5030 Communications & Security_Closed Circuit Surveillance | 0.15544 |  | 0.5285 |  | 1.9119 |  | 3.4663 | Replace | 2.23 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Access Control System | D5030 Communications & Security_Access Control System | 0.10881 |  | 0.3886 |  | 1.5544 |  | 3.1088 | Replace | 2 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Intrusion Alarm System | D5030 Communications & Security_Intrusion Alarm System | 0.10881 |  | 0.2487 |  | 1.1347 |  | 2.3316 | Replace | 1.5 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Fire Alarm / Detection | D5030 Communications & Security_Fire Alarm / Detection | 0.34197 |  | 0.73057 |  | 3.3109 |  | 6.6062 | Replace | 4.25 | Replace | 0
D SERVICES | D50 Electrical | D5030 Communications & Security | Lighting Control System | D5030 Communications & Security_Lighting Control System | 0.17098 |  | 0.3886 |  | 1.3057 |  | 2.487 | Replace | 1.6 | Replace | 0
D SERVICES | D50 Electrical | D5090 Other Electrical Systems | NOT USED | D5090 Other Electrical Systems_NOT USED | [7 empty] | Replace |  | Replace | 0
E EQUIPMENT & FURNISHINGS
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1010 Commercial Equipment | Food Service | E1010 Commercial Equipment_Food Service | 0.69948 |  | 1.1347 |  | 1.399 |  | 3.6528 | Replace | 2.85 | Replace | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1010 Commercial Equipment | Vocational | E1010 Commercial Equipment_Vocational | 2.1712 |  | 5.5106 |  | 10.8914 |  | 39.1878 | Replace | 2.66 | Replace | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Science | E1020 Institutional Equipment_Science | 2.5938 |  | 6.5847 |  | 13.0143 |  | 46.8261 | Replace | 4.46 | Replace | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Art | E1020 Institutional Equipment_Art | 2.3343 |  | 3.6934 |  | 7.375 |  | 32.45 | Replace | 4.31 | Replace | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Stage Performance | E1020 Institutional Equipment_Stage Performance | 7.434 |  | 17.8416 |  | 37.17 |  | 89.208 | Replace | 35000 | Replace | 0 | Cost/SF of Stage Performance Area
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1020 Institutional Equipment | Restroom Accessories/Stalls | E1020 Institutional Equipment_Restroom Accessories/Stalls | 0.28816 |  | 1.6634 |  | 0.51082 |  | 2.5934 | Replace | 1.48 | Replace | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1030 Vehicular Equipment | NOT USED | E1030 Vehicular Equipment_NOT USED | [7 empty] | Replace |  | Replace | 0
E EQUIPMENT & FURNISHINGS | E10 Equipment | E1090 Other Equipment | NOT USED | E1090 Other Equipment_NOT USED | [7 empty] | Replace |  | Replace | 0
E EQUIPMENT & FURNISHINGS | E20 Furnishings | E2010 Fixed Furnishings | blank | E2010 Fixed Furnishings_blank | 2.0502 |  | 3.4662 |  | 5.5165 |  | 13.747 | Replace | 16.32 | Replace | 0
E EQUIPMENT & FURNISHINGS | E20 Furnishings | E2020 Movable Furnishings | blank | E2020 Movable Furnishings_blank | 13.098 |  | 0 |  | 0 |  | 31.4352 | Replace | 24 | Replace | 0
F SPECIAL CONSTRUCTION & DEMOLITION - NOT USED
G BUILDING SITE WORK
G BUILDING SITE WORK | G10 Site Preparation | E2020 Movable Furnishings | NOT USED | E2020 Movable Furnishings_NOT USED
G BUILDING SITE WORK | G20 Site Improvements | G2010 Roadways | blank | G2010 Roadways_blank | 2.0564 |  | 5.2392 |  | 8.5137 |  | 10.4784 | Replace | 8 | Replace | 0 | Cost/SF of surface area
G BUILDING SITE WORK | G20 Site Improvements | G2020 Parking Lots | blank | G2020 Parking Lots_blank | 2.0564 |  | 5.2392 |  | 8.5137 |  | 10.4784 | Replace | 8 | Replace | 0 | Cost/SF of surface area
G BUILDING SITE WORK | G20 Site Improvements | G2030 Pedestrian Paving | blank | G2030 Pedestrian Paving_blank | 2.6196 |  | 5.8941 |  | 11.7882 |  | 14.4078 | Replace | 11 | Replace | 0 | Cost/SF of surface area
G BUILDING SITE WORK | G20 Site Improvements | G2040 Site Development | blank | G2040 Site Development_blank | 7.8588 |  | 10.4784 |  | 32.745 |  | 45.843 | Replace | 35 | Replace | 0 | Cost/LF of fencing
G BUILDING SITE WORK | G20 Site Improvements | G2050 Landscaping | blank | G2050 Landscaping_blank | 2.6196 |  | 2.8816 |  | 3.0125 |  | 3.2745 | Replace | 2.5 | Replace | 0 | Cost/SF of irrigated area
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3010 Water Supply | Domestic | G3010 Water Supply_Domestic | 0 |  | 0 |  | 0 |  | 92.807 | Replace | 65 | Replace | 0 | Cost/LF of pipe
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3010 Water Supply | Fire | G3010 Water Supply_Fire | 0 |  | 0 |  | 0 |  | 92.807 | Replace | 65 | Replace | 0 | Cost/LF of pipe
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3020 Sanitary Sewer | blank | G3020 Sanitary Sewer_blank | 0 |  | 0 |  | 0 |  | 64.251 | Replace | 45 | Replace | 0 | Cost/LF of pipe
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3030 Storm Sewer | blank | G3030 Storm Sewer_blank | 2.95 |  | 4.425 |  | 5.9 |  | 10.325 | Replace | 2.46 | Replace | 0 | Cost/SF of area to be drained
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3040 Heating Distribution | blank | G3040 Heating Distribution_blank | 0 |  | 0 |  | 0 |  | 437.294 | Replace | 225 | Replace | 0 | Cost/LF of HHW/Steam piping
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3050 Cooling Distribution | blank | G3050 Cooling Distribution_blank | 0 |  | 0 |  | 0 |  | 630.7125 | Replace | 225 | Replace | 0 | Cost/LF of CHW piping
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3060 Fuel Distribution | blank | G3060 Fuel Distribution_blank | 0 |  | 0 |  | 0 |  | 78.529 | Replace | 35 | Replace | 0 | Cost/LF of gas piping
G BUILDING SITE WORK | G30 Site Mechanical Utilities | G3090 Other Site Mechanical Utilities | blank | G3090 Other Site Mechanical Utilities_blank | [7 empty] | Replace |  | Replace | 0
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4010 Electrical Distribution | Service | G4010 Electrical Distribution_Service | 0 |  | 0 |  | 1.2998 |  | 3.9932 | Replace | 2.48 | Replace | 0
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4010 Electrical Distribution | Generator | G4010 Electrical Distribution_Generator | 2737.6 |  | 13688 |  | 88972 |  | 123192 | Replace | 30000 | Replace | 0 | Cost/occurrence
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4020 Site Lighting | blank | G4020 Site Lighting_blank | 5129.52 |  | 0 |  | 0 |  | 8704.64 | Replace | 1.3 | Replace | 0 | Cost/occurrence
G BUILDING SITE WORK | G40 Site Electrical Utilities | G4030 Site Communications & Security | blank | G4030 Site Communications & Security_blank | 0 |  | 0 |  | 0 |  | 18.6528 | Replace | 0.8 | Replace | 0
Note on C10: Standard spread and strip / perimeter footings
Note on F10: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on J10: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C11: Pilings or other extended foundation systems that overcome non-standard soil conditions
Note on F11: Minor cracking observed - fill and seal the cracks to prevent water intrusion
Note on J11: Settlement observed in surrounding conditions - requiring stabilization of the foundation, sub-grade adjustment, and re-enforcement of the foundation
Note on C12: Standard ground-set concrete slab. If slab is elevated (i.e. has a crawl space or basement), apply conditions to B1010 instead
Note on H12: Separation cracks occurring requiring route and fill and patch
Note on J12: Differential settlement occurring - requires removal of section of slab, adjustment to sub-grade, and new infill
Note on C15: Assumed as concrete walls with water-proofing on the exterior. Includes only the structural portion and not the wall finishes
Note on F15: Inadequate below grade venting is observed - cut in and add venting
Note on H15: Wall is cracked and spalling requiring route and fill and patch and re-finish
Note on J15: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied
Note on C18: A suspended floor including the structural members and floor construction, but not including the actual finish
Note on H18: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on L18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on N18: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on H19: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on L19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on N19: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on H20: Deck lifting, settling, or uneven - appears related to the deck itself and not the structural support below - requires removal and replacement of deck
Note on L20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on N20: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Note on C21: The roof structure referring to the supporting structure and the deck but excluding the roofing itself
Note on J21: Evidence of a spongy decking from water intrusion - replacing the deck but not the trusses
Note on L21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on N21: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on J22: Evidence of a flexing decking from water intrusion / rust - replacing the deck but not the trusses
Note on L22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on N22: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on J23: Evidence of a spongy / spalling deck from water intrusion - replacing the deck but not the beams
Note on L23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on N23: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Note on F25: Surface is in tact but finish is deteriorated - paint
Note on H25: Cracks visible - route and patch prior to painting
Note on J25: Cracks visible - route and patch prior to painting
Note on F26: Surface is in tact but finish is deteriorated - paint
Note on H26: Some blocks are damaged, needing patch and repair prior to sealing or painting
Note on J26: Some blocks are damaged, needing patch and repair prior to sealing or painting
Note on L26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on N26: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on F27: Surface is in tact but finish is deteriorated - paint
Note on H27: A number of panels are damaged, requiring patch and repair prior to re-painting
Note on J27: A number of panels are damaged, requiring patch and repair prior to re-painting
Note on L27: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on N27: The panels are lifting or separating or otherwise losing their integrity - remove and replace
Note on F29: Surface is in tact but finish is deteriorated - paint
Note on H29: Cracks visible - route and patch prior to painting
Note on J29: Cracks visible - route and patch prior to painting
Note on L29: System in failure with evidence of water intrusion - remove and replace
Note on N29: System in failure with evidence of water intrusion - remove and replace
Note on F30: Minor repairs needed to mortar, prep, and re-sealing
Note on H30: Mortar missing in a majority of areas requiring complete re-pointing and sealing
Note on J30: Mortar missing in a majority of areas requiring complete re-pointing and sealing
Note on L30: Masonry visibly damaged and requiring removal and replacement
Note on N30: Masonry visibly damaged and requiring removal and replacement
Note on F31: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H31: The glazing is double pane but is broken or fogged and requires replacement
Note on J31: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on L31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on N31: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D32: This assumes both individual aluminum windows and storefront systems
Note on F32: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H32: The glazing is double pane but is broken or fogged and requires replacement
Note on J32: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on L32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on N32: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D33: This assumes a metal windows system clad with wood or vinyl
Note on F33: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H33: The glazing is double pane but is broken or fogged and requires replacement
Note on J33: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on L33: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on N33: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on F34: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H34: Minor leaks at wall seams - re-caulk and re-seal
Note on J34: Window panels fogged and require replacement
Note on L34: Settlement or displacement is evident
Note on N34: Settlement or displacement is evident
Note on H35: Door hardware is damaged or non-functional and requires replacement
Note on J35: Door panel and hardware are damaged and require replacement
Note on L35: Door frame, door, and hardware are damaged and require replacement
Note on N35: Door frame, door, and hardware are damaged and require replacement
Note on H36: Door hardware is damaged or non-functional and requires replacement
Note on J36: Door panel and hardware are damaged and require replacement
Note on L36: Door frame, door, and hardware are damaged and require replacement
Note on N36: Door frame, door, and hardware are damaged and require replacement
Note on F37: Minor Dings or Bends
Note on H37: Door hardware is damaged or non-functional and requires replacement
Note on J37: Door panel and hardware are damaged and require replacement
Note on L37: Door frame, door, and hardware are damaged and require replacement
Note on N37: Door frame, door, and hardware are damaged and require replacement
Note on D38: Apply to door count
Note on F38: Minor Dings or Bends
Note on H38: Door hardware is damaged or non-functional and requires replacement
Note on J38: Door panel and hardware are damaged and require replacement
Note on L38: Door track system, door panel, and hardware are damaged and require replacement.
Note on N38: Door frame, door, and hardware are damaged and require replacement
Note on D39: Apply to door count
Note on F39: Minor Dings or Bends
Note on H39: Door hardware is damaged or non-functional and requires replacement
Note on J39: Door panel and hardware are damaged and require replacement
Note on L39: Door track system, door panel, and hardware are damaged and require replacement.
Note on N39: Door frame, door, and hardware are damaged and require replacement
Note on C41: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts
Note on F41: Small number of shingles lifting and/or separation in a portion of flashing
Note on H41: Leaks in a specific area or zone related to poor detailing and or flashing
Note on J41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on L41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on N41: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on F42: Small number of shingles lifting and/or separation in a portion of flashing
Note on H42: Leaks in a specific area or zone related to poor detailing and or flashing
Note on J42: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on L42: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on F43: Small number of shingles lifting and/or separation in a portion of flashing
Note on H43: Leaks in a specific area or zone related to poor detailing and or flashing
Note on J43: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on L43: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on H44: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations
Note on L44: Tiles are cracked, loose, or damaged and require removal and replacement
Note on N44: Tiles are cracked, loose, or damaged and require removal and replacement
Note on F45: Minor blistering requiring isolated patches
Note on H45: Leaks in a specific area or zone related to poor detailing and or flashing or unchecked blisters
Note on J45: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Replace roof system OVER TOP OF EXISTING
Note on L45: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on N45: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on F46: Minor blistering requiring isolated patches
Note on H46: Leaks in a specific area or zone related to poor detailing and or flashing or seam separation
Note on J46: System in complete failure with multiple leaks and multiple examples of visible breaches in system - Prep and re-coat roof system OVER TOP OF EXISTING
Note on L46: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on N46: System in complete failure with multiple leaks and multiple examples of visible breaches in system - REMOVE AND Replace roof system
Note on H47: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant
Note on L47: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on N47: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Note on H48: Leaks occurring at isolated areas requiring grout removal and re-grout at isolated tile locations
Note on L48: Tiles are cracked, loose, or damaged and require removal and replacement
Note on N48: Tiles are cracked, loose, or damaged and require removal and replacement
Note on H49: Minor leaking is occurring, requiring re-caulk and re-seal
Note on L49: The panes or framing are damaged beyond repair and requires replacement
Note on N49: The panes or framing are damaged beyond repair and requires replacement
Note on L50: The door is non-functional or damaged beyond repair and requires replacement
Note on N50: The door is non-functional or damaged beyond repair and requires replacement
Note on L53: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on N53: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on J54: There are some blocks that are damaged and requires a strategic removal and replacement
Note on L54: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on N54: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Note on F55: Minor Damage not requiring replacement of frame
Note on H55: There are some sections which are damaged and requires a strategic removal and replacement
Note on J55: There is evidence of settling, failure, or a compromised structure that requires removal and replacement. Frame only no windows
Note on L55: There is evidence of settling, failure, or a compromised structure that requires removal and replacement. Including Windows
Note on H56: Door hardware is damaged or non-functional and requires replacement
Note on J56: Door panel and hardware are damaged and require replacement
Note on L56: Door frame, door, and hardware are damaged and require replacement
Note on N56: Door frame, door, and hardware are damaged and require replacement
Note on H57: Door hardware is damaged or non-functional and requires replacement
Note on J57: Door panel and hardware are damaged and require replacement
Note on L57: Door frame, door, and hardware are damaged and require replacement
Note on N57: Door frame, door, and hardware are damaged and require replacement
Note on F58: Minor Dings or Bends
Note on H58: Door hardware is damaged or non-functional and requires replacement
Note on J58: Door panel and hardware are damaged and require replacement
Note on L58: Door frame, door, and hardware are damaged and require replacement
Note on N58: Door frame, door, and hardware are damaged and require replacement
Note on F59: Minor Dings or Bends
Note on H59: Door hardware is damaged or non-functional and requires replacement
Note on J59: Door panel and hardware are damaged and require replacement
Note on L59: Door track system, door panel, and hardware are damaged and require replacement.
Note on N59: Door frame, door, and hardware are damaged and require replacement
Note on F60: Minor Dings or Bends
Note on H60: Door hardware is damaged or non-functional and requires replacement
Note on J60: Door panel and hardware are damaged and require replacement
Note on L60: Door track system, door panel, and hardware are damaged and require replacement.
Note on N60: Door frame, door, and hardware are damaged and require replacement
Note on F61: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H61: The glazing is double pane but is broken or fogged and requires replacement
Note on J61: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on L61: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on N61: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D62: This assumes both individual aluminum windows and storefront systems
Note on F62: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H62: The glazing is double pane but is broken or fogged and requires replacement
Note on J62: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on L62: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on N62: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on D63: This assumes a metal windows system clad with wood or vinyl
Note on F63: Minor repairs to glazing, sealing, or sash. Does not require replacement
Note on H63: The glazing is double pane but is broken or fogged and requires replacement
Note on J63: The glazing is single pane or the sash is damaged - either requires replacement of the sash and its glazing
Note on L63: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on N63: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Note on J65: Rails not compliant with code and require removal and replacement
Note on L65: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on N65: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on F66: Rust visible - prep and re-finish
Note on J66: Rails not compliant with code and require removal and replacement
Note on L66: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on N66: Structural integrity of stair unit is compromised and requires its removal and replacement
Note on J67: An isolated structural crack or separation requiring re-enforcement in place
Note on L67: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on N67: Structural cracking and separation occurring in multiple locations - remove and replace the stair unit
Note on F68: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal
Note on L68: Severe cracking requiring removal and replacement of tread in fills
Note on N68: Severe cracking requiring removal and replacement of tread in fills
Note on L69: finish is lifting or separating and creating trip hazards - remove and replace
Note on N69: finish is lifting or separating and creating trip hazards - remove and replace
Note on F73: Surface is in tact but finish is deteriorated - paint
Note on L73: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on N73: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on F74: Surface is in tact but finish is deteriorated - paint
Note on H74: Surface is damaged - patching of the surface is required prior to painting
Note on L74: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on N74: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on F75: Surface is in tact but finish is deteriorated - paint
Note on L75: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on N75: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on F79: Grout is damaged or deteriorated
Note on L79: Tiles are cracked or in disrepair
Note on N79: Tiles are cracked or in disrepair
Note on L80: worn or severely stained or starting to pull up / bubble
Note on N80: worn or severely stained or starting to pull up / bubble
Note on F81: sporadic number of tiles are lifting or cracked / broken and require replacement
Note on J81: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are NOT asbestos
Note on L81: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on N81: The majority of tiles are lifting, cracking / broken and require replacement - the tiles or glue are asbestos
Note on L82: Severely worn or seams separating - replace
Note on N82: Severely worn or seams separating - replace
Note on F83: Surface feels rough and/or taking in moisture from the surface resulting in staining - prep and re-seal
Note on L83: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on N83: Significant cracking, but not differential - requires prep and crack filling prior to re-seal. If differential, refer to slab on grade of floor construction above
Note on F84: Grout is damaged or deteriorated
Note on L84: Tiles are cracked or in disrepair
Note on N84: Tiles are cracked or in disrepair
Note on L85: Systemic blistering or severely worn traffic areas - strip and replace
Note on N85: Systemic blistering or severely worn traffic areas - strip and replace
Note on H86: Surface is damaged - requires sanding, repair, and re-coat / re-stripe
Note on L86: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on N86: Wood planks are deteriorated, separating, and multiple dead spots - replace floor
Note on F87: Surface is in tact but finish is deteriorated - paint
Note on H87: Surface is damaged - patching of the surface is required prior to painting
Note on L87: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on N87: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on F88: Stained or damaged ceiling tiles
Note on H88: Diagonal bracing missing from grid
Note on L88: Grid is sagging with tiles compromised - requires replacement of system
Note on N88: Grid is sagging with tiles compromised - requires replacement of system
Note on F89: Stained or damaged ceiling tiles
Note on L89: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on N89: Systemic failure of finish, possible water intrusion - requires removal and replacement
Note on L91: Surface is in tact but finish is deteriorated - paint
Note on N91: Surface is in tact but finish is deteriorated - paint
Note on C94: Assume standard cab-style elevator
Note on F94: The elevator doors are damaged and require replacement
Note on H94: Electrical components are not working
Note on J94: Replacement of the hoist cables, guide rails, or other similar mechanical components is required
Note on L94: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on N94: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on H95: Electrical components are not working
Note on L95: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on N95: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C96: Assume open vertical or inclined lift
Note on H96: Electrical components are not working
Note on L96: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on N96: Mechanical and electrical components have deteriorated requiring the replacement of the system
Note on C98: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here
Note on H98: Flush valves or faucets are non-functional and require replacement
Note on L98: The fixture itself is broken or is not compliant with water efficiency standards
Note on N98: The fixture itself is broken or is not compliant with water efficiency standards
Note on F99: The vale stems, pressure gauges, and gate valves no longer function.
Note on H99: The insulation on the piping is in disrepair, loose, or missing.
Note on L99: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on N99: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on F100: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains
Note on L100: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on N100: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Note on C101: This is for the presence of interior rain drains; note building percentage based on area of roof served - excludes external downspouts
Note on H101: The rain drain or overflow is damaged and needs replacement
Note on L101: The integrity of the piping is compromised and is leaking inside the walls
Note on N101: The integrity of the piping is compromised and is leaking inside the walls
Note on C104: This assumes gas piping
Note on F104: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on L104: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on N104: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on F105: The burner is inefficient and requires refurbishment
Note on H105: One major component needs to be replaced
Note on J105: More than one major component needs to be replaced
Note on L105: The system is in failure
Note on N105: The system is in failure
Note on J106: Some of the distribution fans and coils are dysfunctional.
Note on L106: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on N106: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on H107: A small number of minor parts need to be repaired or replaced
Note on J107: The burner, combustion chamber, or fan are faulty and require replacement
Note on L107: The entire furnace requires replacement
Note on N107: The entire furnace requires replacement
Note on H108: A small number of minor parts need to be repaired or replaced
Note on J108: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger
Note on L108: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on N108: System operates at low efficiency with corrosion and leaks apparent. Replace system
Note on J109: Some of the distribution fans and coils are dysfunctional.
Note on L109: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on N109: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Note on L110: The chiller is beyond economic repair
Note on N110: The chiller is beyond economic repair
Note on H111: Dampers in the system are inoperative
Note on J111: The insulation is damaged or missing
Note on L111: The ductwork is damaged or inadequately designed and requires replacement
Note on N111: The ductwork is damaged or inadequately designed and requires replacement
Note on F112: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Note on H112: The insulation on the piping is in disrepair, loose, or missing.
Note on L112: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on N112: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Note on L113: Entire unit is failing to function
Note on N113: Entire unit is failing to function
Note on H114: Internal compressor is bad and requires replacement
Note on L114: Entire unit is failing to function
Note on N114: Entire unit is failing to function
Note on F115: In-room valve is failing and requires replacement
Note on L115: Entire unit is failing to function
Note on N115: Entire unit is failing to function
Note on J116: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators
Note on L116: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on N116: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system - replace
Note on L117: One or more zones require re-balancing
Note on N117: One or more zones require re-balancing
Note on H120: Sprinkler heads are inoperable or non-compliant and need to be replaced
Note on L120: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on N120: The piping has deteriorated or clogged or is non-compliant and needs to be replaced, including heads
Note on H121: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced
Note on L121: The fire pump is beyond repair and needs to be replaced
Note on N121: The fire pump is beyond repair and needs to be replaced
Note on C122: Assume chemical extinguishing system
Note on H122: The back-up tank has been discharged or lacks pressure and needs to be replaced
Note on L122: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on N122: The system is non-functional or not compliant with the current needs and needs to be replaced
Note on H125: Wiring has systemic problems or does not meet code and needs to be replaced
Note on J125: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement
Note on L125: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on N125: Main switchgear is obsolete or undersized and requires replacement, including service into building
Note on J126: The lighting fixtures are obsolete or non-functional and require replacement
Note on L126: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on N126: Replacement of fixtures is requiring the replacement of the wiring as well - includes fixtures AND wiring
Note on H127: There are individual devices that are not functional.
Note on J127: The master control panel is obsolete or not functional
Note on L127: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on N127: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H128: There are individual devices that are not functional.
Note on J128: The master control panel is obsolete or not functional
Note on L128: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on N128: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H129: There are individual devices that are not functional.
Note on J129: The master control panel is obsolete or not functional
Note on L129: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on N129: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H130: There are individual devices that are not functional.
Note on J130: The master control panel is obsolete or not functional
Note on L130: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on N130: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H131: There are individual devices that are not functional.
Note on J131: The master control panel is obsolete or not functional
Note on L131: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on N131: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Note on H132: There are individual devices that are not functional or in regular alarm
Note on J132: The master control panel is obsolete or not functional
Note on L132: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on N132: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Note on F133: Individual room sensors are failing and require replacement
Note on J133: The central control panel and software need upgraded
Note on L133: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on N133: The entire system is in failure and requires replacement of sensors, wiring and central panel
Note on F138: 2-3 pieces of equipment require replacement
Note on H138: Counters and sinks are not code compliant and require replacement with stainless steel and sink system
Note on J138: Walk-in cooler and freezer are not functional or function intermittently and require replacement
Note on L138: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on N138: Walk-ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Note on F139: 2-3 pieces of equipment require replacement
Note on J139: Mechanical and electrical service upgrades are required to meet code and amount of program equipment
Note on L139: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on N139: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Note on H140: Room lacking (and needing) eye wash or fume hood
Note on J140: Sinks are in disrepair and require replacement
Note on L140: Work stations need upgrades to meet current program criteria - replace
Note on N140: Work stations need upgrades to meet current program criteria - replace
Note on H141: Storage units damaged or in disrepair
Note on J141: Sinks are in disrepair and require replacement
Note on L141: Work stations need upgrades to meet current program criteria - replace
Note on N141: Work stations need upgrades to meet current program criteria - replace
Note on H142: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded
Note on J142: Fly rigging in disrepair and needs upgrading
Note on L142: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on N142: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Note on F143: An accessory is damaged or missing
Note on H143: Accessories need to be replaced to meet ADA
Note on J143: The stall doors are not functional or missing and need to be replaced
Note on L143: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on N143: The restrooms stall structure is failing or needs re-configuration and needs to be replaced
Note on D144: Note anything specific in the "Other" category at the bottom of the assessment form
Note on C147: Assume fixed casework (counters, cabinets, shelving, etc.)
Note on F147: The counter top or exposed surface has been damaged and can be refinished
Note on H147: The drawers and/or doors are damaged and require replacement including hardware
Note on J147: A combination of minor and moderate action is required, but the box is still salvageable
Note on L147: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on N147: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Note on C148: Assume loose furnishings (desks, chairs, tables, etc.)
Note on L148: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on N148: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Note on C154: Paved only or needs to be paved
Note on F154: Minor cracking exists and can be resolved with application of a slurry coat
Note on J154: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Note on L154: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on N154: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Note on C155: Paved only or needs to be paved
Note on F155: Minor cracking exists and can be resolved with application of a slurry coat
Note on J155: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Note on L155: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on N155: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over-ex of sub-grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Note on C156: Concrete only or needs to be concrete
Note on J156: Sections are broken with differential settlement requiring the removal of the effected panels and replacement
Note on L156: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on N156: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub-grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Note on C157: Chain-link fencing
Note on J157: The fence fabric is damaged and needs to be replaced
Note on L157: The fencing has lost its structural integrity and is beyond repair.
Note on N157: The fencing has lost its structural integrity and is beyond repair.
Note on C158: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form
Note on L158: Irrigation system is dysfunctional and beyond repair
Note on N158: Irrigation system is dysfunctional and beyond repair
Note on D160: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form
Note on L160: A portion of the line has lost its structural integrity and requires replacement
Note on N160: A portion of the line has lost its structural integrity and requires replacement
Note on D161: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form
Note on L161: A portion of the line has lost its structural integrity and requires replacement
Note on N161: A portion of the line has lost its structural integrity and requires replacement
Note on C162: Lines only. Septic fields, tanks, etc. should be placed in "other" category at bottom of form
Note on L162: A portion of the line has lost its structural integrity and requires replacement
Note on N162: A portion of the line has lost its structural integrity and requires replacement
Note on C163: Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form
Note on F163: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign
Note on H163: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Note on J163: Detention/retention has failed, but piping and catch basins are functional. Replace detention / retention system
Note on L163: The entire underground system has failed and requires removal and replacement of all components
Note on N163: The entire underground system has failed and requires removal and replacement of all components
Note on L164: A portion of the line has lost its structural integrity and requires replacement
Note on N164: A portion of the line has lost its structural integrity and requires replacement
Note on L165: A portion of the line has lost its structural integrity and requires replacement
Note on N165: A portion of the line has lost its structural integrity and requires replacement
Note on C166: Natural gas lines
Note on L166: A portion of the line has lost its structural integrity and requires replacement
Note on N166: A portion of the line has lost its structural integrity and requires replacement
Note on D169: Assumes the private portion of the service lines typically underground after the meter or transformer
Note on J169: The transformer no longer functions and is in need of replacement
Note on L169: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on N169: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Note on F170: The generator needs to be tuned up
Note on H170: The valves or other engine parts need to be repaired or replaced and then a tune up
Note on J170: Generator is non-functional or under-sized
Note on L170: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on N170: The system (generator, tank, services lines connected lighting system) is non-functional or under-sized
Note on H171: The fixtures are nonfunctional and require replacement
Note on L171: The fixtures, supports, and underground wiring need to be replaced
Note on N171: The fixtures, supports, and underground wiring need to be replaced
Note on C172: Assumes low voltage lines underground
Note on L172: Site cabling is inadequate or service is interrupted - replace cabling
Note on N172: Site cabling is inadequate or service is interrupted - replace cabling

## Building Type Budget-READ ONLY
Budgeted Replacement Cost of Buildings by Type
| Edit Raw Budget to match local current pricing | Cost Factor, Inflation & Soft Costs entered in Base Information Sheet
Type | Raw Budget / SF | x Cost Factor | x Inflation | x Soft Costs | Forwarded FCI Budget
Elementary School | 348 | 0 | 0 | 0 | 0
Middle School | 392 | 0 | 0 | 0 | 0
K-8 School | 392 | 0 | 0 | 0 | 0
High School | 427 | 0 | 0 | 0 | 0
Gymnasium Building | 481.5 | 0 | 0 | 0 | 0
Pool Building | 594.92 | 0 | 0 | 0 | 0
Vocational Building | 410 | 0 | 0 | 0 | 0
Administrative Building | 350 | 0 | 0 | 0 | 0
Maintenance Building | 410 | 0 | 0 | 0 | 0
Storage Building | 310 | 0 | 0 | 0 | 0
Warehouse | 310 | 0 | 0 | 0 | 0
Food Services Building | 508.25 | 0 | 0 | 0 | 0
Bus Shelter | 310.3 | 0 | 0 | 0 | 0
Bus Garage | 326.35 | 0 | 0 | 0 | 0
Athletic Grandstand | 30 | 0 | 0 | 0 | 0
Large Greenhouse | 165 | 0 | 0 | 0 | 0
Other Commercial | 359.52 | 0 | 0 | 0 | 0
|  |  |  | FCI Reference | 1
Note:
Small support out buildings shall be assessed as "other" under the primary building assessment and not as their own building assessment
The Raw Budget number includes all cost associated with a contractors bid number on bid day. |  |  |  | Name of the company performing the assessment
Initial Assessor Name:
The Raw Budget number does not include any value for additional FFE (Fixtures/Furnishings/Equipment)
The Raw Budget number does not include any value for Owner/PM Overhead management fees.
The Raw Budget number does not include any value for "Extensive Testing" other than testing noted in standard specifications.

## Dashboard Integration Page (hidden)
Dashboard Integration Page
Scorecard Categories - Condition Assessment- | PCA Raw Comment Links | Assessor Narrative | Assessor Rating Red, Yellow, Green | To copy & paste PCA Raw Comments: Copy the text. Right click and choose paste option "Values (V)". |  |  |  |  | Assessor Narrative | Assessor Rating Red, Yellow, Green
Exterior Structure | 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | Select a color rating from the dropdown only. The first letter of the color must be capitalized. | Green |  |  |  | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Interior Structure | 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green |  | Yellow |  |  |  | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Foundation | 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | If the narrative is "Included in Main Building report" or something similar, still choose a color rating based on how the category is rated in the referenced workbook. | Red |  |  |  | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
HVAC/Plumbing | 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 0 | HVAC: None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. Plumbing: None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | #DIV/0! |  |  | 0 | 0 | #DIV/0! | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs.: None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs.: | #DIV/0!
Roofing | 0 0 0 0 0 0 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
ADA | 0 | 0 | 0 | Use consistent punctuation throughout all narratives. |  |  |  |  | 0 | 0
Parking/Traffic | 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Furnishing, Fixtures, Equipment | 0 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | Run a spell check after completing this sheet. |  |  |  |  | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Site | 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Electrical | 0 0 0 0 0 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Doors | 0 0 0 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Safety/Security | 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Exterior/Interior Windows | 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Flooring | 0 0 0 0 0 0 0 | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green | [5 empty] | None of this system requires major renovation or replacement. The cost to address identified needs is <1% of estimated cost to replace them, indicating need for regular maintenance and repairs. | Green
Line items from PCA "Other" section. [For reference only; does not populate on Dashboard]
Priority Projects | Priority 1: Mission Critical Priority 2: Indirect Impact To The Building Priority 3: Recommended |  |  | Use a period after each Priority Project line item (this is how Dashboard knows to separate line items). If you want to combine two comments into one line item, separate them by a semicolon. i.e., Replace HVAC system components at end of useful life; test and balance new HVAC systems. Dashboard would publish this as ONE recommendation. Make sure there are no spaces after the last sentence in the Priority/Additional Projects cells. EXAMPLES OF PRIORITY PROJECTS Please add your own commentary specific to this facility in cell B19. Separate line items with periods. Roof is nearing end of useful life, is worn, and in need of replacement. Many of the HVAC system and supporting exterior electrical components are nearing the end of their useful life. Playground equipment, drainage, and fall protection in need of repair.
Additional Projects if Funds Become Available |  |  |  | EXAMPLES OF ADDITIONAL PROJECTS Please add your own commentary specific to this facility in cell B20. Separate line items with periods. Exterior windows need re-caulking and repair. Brick veneer expansion joints and weep holes need repair or replacement. Parking lot and driveway asphalt needs resealing. Erosion in rear of facility should be corrected. Minor ADA improvements need to be made to front of the building and various restrooms.
Scorecard Categories - Educational Adequacy Assessment- | Assessor Narrative | Assessor Rating Red, Yellow, Green | N/A | If a category is not applicable to this site, leave the ASSESSOR NARRATIVE and COLOR RATING cells blank & put "N/A" in column D.
Core Classrooms
Special Education
Visual and Performing Arts
Physical Education
Cafeteria
Library | 1 |  | Insert an estimated local cost inflation factor based on how much local costs are greater/lesser than the base prices in the PCA Cost Tables. (E.g., 1.15 = costs are ~ 15% greater than the average in the PCA Cost Table. If costs are considered average, keep the value "1")
Occupant Flow
Administration |  |  | Name of the company performing the assessment
Security | See Safety & Security recommendations on the Facility Details page.
Site Athletics
Site Playgrounds/Extracurricular
VoAg or CTE
Actions to improve the educational environment |  |  |  | EXAMPLE OF ACTIONS TO IMPROVE… Please add your own commentary specific to this facility in cell B35. The educational environment of the facility is in good condition. Security enhancements to campus should be made. Minor maintenance such as window resealing and chalkboard replacement are needed.
Current Enrollment | 0
Functional Capacity | 0 |  |  | Use studometer to populate data.
Current Capacity | #DIV/0!
Educational Programming | Disregard this section. Educational Programming is no longer published on Dashboard.
B SHELL |  |  |  | EXAMPLE OF EXECUTIVE SUMMARY Please add your own commentary specific to this facility in cell B41. Built in 1998, the Copperfield Elementary School facility is in good condition but is in need of maintenance and repair of various building components. The roof should be replaced due to age and substantial degranulation and older HVAC system components should be addressed at the time of replacement. In addition, security fencing should be installed. In all, the interior of the facility is in good condition and provides a well-maintained educational environment that is conducive to learning. With adequate maintenance, the campus should continue to serve the district for an additional 25-30 years.
Insert information below from "Physical Condition Assessment Sheet"
Physical Condition Budget Sub-Total | 0
Budgeted Development Costs | 0
Physical Condition Budget TOTAL | 0
Cost with Escalation to June 2021 | 0
Cost with Escalation to June 2022 | 0
Cost with Escalation to June 2023 | 0
Replacement Budget | 0
Facility Condition Index (FCI) | #DIV/0!
Insert information below from "Base Information Sheet"
District Name: | 0
Site Name: | 0
Building Name: | 0
Building Type: | Elementary School
Physical Address of Building: | 0
Original Year Built, Years of Additions: | 0
County: | 0
Gross Square Footage: | 0 |  |  | B61 & C61 is where you will enter other buildings/additions/renovations at this site. Enter the name (B61) and construction date (C61). Use the exact format below (no spaces between years).
Site Acreage: | 0
Campus History: |  |  |  | B61: Original Main Building, Gym, Cafeteria Building C61: 1984,1996,2005
Populated from the Additions fields in the Renovations, Additions & Prtbls | 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
| 0 | 0
Note on A61: Tiffany Hammond: Separate each item by a comma.
Note on A62: Tiffany Hammond: Complete the ADDITIONS section on the "Renovations, Additions, & Portables" tab. If multiple buildings are grouped in with this Site, itemize them out here.

## Edu Capacity Calculation (hidden)
District/Campus? | [6 empty] | Hide rows not used, do not delete rows
|  |  |  | You Populate | Auto Populated
Existing Enrollment |  | From Campus Survey
Staff Capacity |  | From Campus Survey
Functional Student Capacity |  | From School Educational Capacity Overview Table | Determine if campus is primary/secondary and if compliant/non-compliant then insert capacity number selected into "Functional Student Capacity" box after completing "Classroom Capacity Section"
Educational Capacity Overview
[5 empty] | 90% of Raw |  | Existing |  | TEA # of recommended labs:
School Type | Room Size | Existing Enrollment | Raw Capacity | % of Raw Capacity | Functional Capacity | % of Functional Capacity | Middle/ Junior High Science | High School Science | Middle/ Junior High Science | High School Science
Primary Schools/Elementary Schools/Early Learning, Pre-K, K, 1st - 6th | Compliant | 0 | 22 | 0% | 19.8 | 0%
| Non-Compliant | 0 | 0 | #DIV/0! | 0 | #DIV/0!
Secondary School/Junior High/High School | Compliant | 0 | 25 | 0% | 22.5 | 0% | 0 | 0 | 0 | 0
| Non-Compliant | 0 | 0 | #DIV/0! | 0 | #DIV/0! | 0 | 0 | 0 | 0
For this worksheet a "Compliant" school is where 85% or more of the classrooms are at least 800 sf. (22 Students per classroom)
For this worksheet a "Non-compliant" elementary is where more than 15% of classrooms are <800 sf.
Classroom Capacity Section
Not Required to use room number
NONCOMPLIANT Pre-K, K, & 1st Rooms Only | # of Rooms | Room Number | Sq. Ft. | Review campus survey to assist in completing table.
| 1 |  | Insert an estimated local cost inflation factor based on how much local costs are greater/lesser than the base prices in the PCA Cost Tables. (E.g., 1.15 = costs are ~ 15% greater than the average in the PCA Cost Table. If costs are considered average, keep the value "1")
Name of the company performing the assessment
General Use Classrooms, Homerooms | # of Rooms | Room # or location | Room SqFt | Review campus survey to assist in completing table.
Specialized Learning Areas, Vocational/ROTC/Special Use Rooms/Band/Art/Choir/Gym Homeroom | # of Rooms* | Room/Program Name | Clrm. Sq. Ft. | Shop Sq. Ft. | Adequate Vent. | Adequate Storage | Hard Floor | Review campus survey to assist in completing table.
* If district is using classroom space as "Homeroom" count classroom for capacity.
Special Instructional Rooms, DAEP, …... |  | Room Number | SqFt | Use | Review campus survey to assist in completing table.
Classroom usually would not be used as Homeroom, don't indicate in # of rooms column. SqFt of room is not added to total SqFt.
Special Education Rooms, Life Skills |  | Room Number | Sq. Ft. | Life Skills Kitchen Area | Changing Area | Restroom | Review campus survey to assist in completing table.
Classroom usually would not be used as Homeroom, don't indicate in # of rooms column. SqFt of room is not added to total SqFt.
Computer labs | # of Rooms* | Room # or location | Classroom/Homeroom SqFt * | Actual SqFt | + / (-) TEA 900 sq. ft. requirement | Maximum number of computers | Current number of computers | PC's + / (-) TEA requirement | Good configuration | Review campus survey to assist in completing table.
* If classroom is used as "Homeroom" use 700SqFt in Classroom SqFt Column and count in # of rooms column. |  |  |  |  | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
[5 empty] | -900 | 0 |  | 0
Science - prim./elem./interim. | # of Rooms* | Room number | Classroom/Homeroom SqFt * | Actual SqFt | + / (-) TEA | Lecture & lab together | Max # of students | Number of lab stations | Adequate storage | Review campus survey to assist in completing table.
* If classroom is used as "Homeroom" use 700SqFt in Classroom SqFt Column and count in # of rooms column. |  |  |  |  | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
Stand alone or single use Science Classrooms, with or without Lab |  |  |  |  | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
If room is a stand-alone lab (not lecture/lab), then change 900 min. to 800 min. |  |  |  |  | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
[5 empty] | -900 |  | 0
Science - middle/junior high | # of Rooms* | Room number | Classroom/Homeroom SqFt * | Actual SqFt | + / (-) TEA ** | Max # of students | Lecture & lab together | Number of lab stations | Actual Counter Length | + / (-) TEA | Eye wash & Shower | Adequate storage | Review campus survey to assist in completing table.
** If room is a stand-alone lab (not lecture/lab), then change 1,200 min. to 1,000 min. |  |  |  |  | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
* If classroom is used as "Homeroom" use 700SqFt in Classroom SqFt Column and count in # of rooms column. |  |  |  |  | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
[5 empty] | -1200 | 0 |  |  |  | 0
Science - high school | # of Rooms* | Room number | Classroom/Homeroom SqFt * | Actual SqFt | + / (-) TEA ** | Max # of students | Lecture & lab together | Number of lab stations | Actual Counter Length | + / (-) TEA | Eye wash & Shower | Adequate storage | Review campus survey to assist in completing table.
** If room is a stand-alone lab (not lecture/lab), then change 1,400 min. to 1,200 min. |  |  |  |  | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
* If classroom is used as "Homeroom" use 700SqFt in Classroom SqFt Column and count in # of rooms column. |  |  |  |  | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
[5 empty] | -1400 | 0 |  |  |  | 0
Mis.
Mis.
Mis.
Mis.
Mis.
Mis.
Mis.
Mis.
Mis.
Total Homerooms | 1 |  | 0 | Total SqFt of Homerooms
|  |  | 0 | Average Room SqFt
Student Support
Nurses clinic | Square Feet | + / (-) recommended | Number of Beds | Number of Private Beds | Restroom within clinic
-500
| Sink | Refrigerator | Hard Floor | Secure Storage | Near front office
Library | Total sq. ft. | 0 | Total of stacks, office, work, Media, & Storage
| TEA recommended sq. ft. | 1400
| + / (-) TEA recommended | -1400
| Meets TEA recommended | No
Stacks sq. ft.
Office sq. ft.
Work Room sq. ft.
Media Room sq. ft.
Storage sq. ft.
Age appropriate space
Furniture condition
Shelving condition
Cafeteria & kitchen | Cafeteria - Seating Area |  |  |  | Serving Area
| Square Feet - Actual | Square Feet - Recommended * | Square Feet + / (-) Recommended | Seating Capacity | Square Feet - Actual | Square Feet - Recommended ** | Square Feet + / (-) Recommended | # of Serving Lines
|  | 0 | 0 |  |  | 0 | 0
|  | * 10 square feet per seat |  |  |  | ** ½ a square feet per seat
| Kitchen |  |  |  |  | Lunch Periods
| Square Feet - Actual | Square Feet - Recommended *** | Square Feet + / (-) Recommended | Total SF Cold & Dry Storage | Projected Average Daily Meals Served by Functional Capacity | # of Lunch Periods | Begins at: | Ends at:
|  | 0 | 0 | 0 | 0 | survey | survey | survey | Need to see survey for information.
|  | *** 3 ½ square feet per meal served |  | Reported Meals Served | Survey
Dry Storage
Food storage
Cold storage, Ref
Cold storage, Fez
Restrooms, Students | Building/Location | Boys Commodes | Urinals | Girls Commodes | Unisex Commodes | Sinks | ADA Compliance Level | Condition of Plumbing Fixtures | Condition of Stall Panels & Hardware | Ventilation
At least one boys and girls restroom per building on an accessible route must be ADA.
Boys commodes: 1 for every 50 male students (use 50% of functional capacity student total)
Boys urinals: 1 for every 100 male students (use 50% of functional capacity student total)
Girls commodes: 1 for every 30 female students (use 50% of functional capacity)
Sinks: 1 for every 40 students
| Totals | 0 | 0 | 0 | 0 | 0
| + / (-) Recommended | 0 | 0 | 0 |  | 0
Restrooms, Staff | Campus/Location | Men's Commodes | Urinals | Women's Commodes | Unisex Commodes | Sinks | ADA Compliance Level | Condition of Plumbing Fixtures | Condition of Stall Panels & Hardware | Ventilation
| Totals | 0 | 0 | 0 | 0 | 0
Drinking fountains | Location | Total of All Fountains on Site | # of Low Fountains, =<36" | 1 drinking fountain for every 150 students
| Totals | 0 | 0
| + / (-) Recommended * | 0 | 0
Teachers' lounge/workroom | Room Number | Square Feet | Function
| Total | 0
| Total recommended | 0
| Difference +/(-) | 0
Parking -- Elem/Interim/MS/JrHS | Area | Regular Spaces | ADA | Van Accessible | Surface Type | Surface Condition | Striping Condition | Lighting | Notes: | Req'd ADA | Van Req'd | Rounded
visitor parking 5% of students | [9 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
| Total | 0 | 0 | 0
| Total recommended/req'd | 0 | 0 | 0 |  | 1
| Difference +/(-) | 0 | 0 | 0
Parking -- High School | Area | Regular Spaces | ADA | Van Accessible | Surface Type | Surface Condition | Striping Condition | Lighting | Notes: | Req'd ADA | Van Req'd | Rounded
vis./stud. parking 25% of students | [9 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
[10 empty] | FALSE | 0 | 0
| Total | 0 | 0 | 0
| Total recommended/req'd | 0 | 0 | 0 |  | 1
| Difference +/(-) | 0 | 0 | 0
Note on J210: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Can instructor see all screens at same time?

## HVAC
| HVAC TABLE | [12 empty] | Age | # of units | Tons | Cost | % of Total Tons
| District: | 0 |  |  |  |  | Sq. Ftg. | 0 |  | Const. Year | 0 | Sq. Ft./Ton | #DIV/0! | 10-14 years old | 0 | 0 | 0 | #DIV/0!
| Campus: | 0 |  |  |  |  | Total Tonnage | 0 |  | Current Year | 2026 | Immediate Need Cost | 0 | 15+ years old | 0 | 0 | 0 | #DIV/0!
[12 empty] | Total Cost | 0 |  | Total Replacement Cost |  | 0
| Cooling Systems: | Water Cooled Chiller | Air Cooled Chiller | Water Source Heat Pumps | Packaged Unit | Split System | Window | Wall | Boiler | DOAU
| Estimate: | 1700 | 2250 | 5500 | 5000 | 5000 | 1750 | 5500 | 100 | 50 |  |  |  | No need to delete unused rows.
| Building | Location of Unit | Area | Manufacturer | Model Number | Serial Number | District ID | Type | Tonnage | CFM/MBH | Year | Age | Replacement Cost
[12 empty] | 0 | 0 | If there is no HVAC present, write "No HVAC system at this site." in cell B12. Then enter "0" in cells N12 and N2.
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0 | If you do not have a replacement cost for a unit, zero out the cost in column N.
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
Initial Assessor Name: | [11 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
[12 empty] | 0 | 0
| Systems |  |  | Location of Unit
| Split System |  |  | Ground
| Air Cooled Chiller |  |  | Roof
| Water Cooled Chiller |  |  | Wall
| Packaged Unit |  |  | Window
| Water Source Heat Pumps |  |  | Attic
| Window |  |  | Closet
| Wall |  |  | Mezzanine
| Boiler |  |  | Mechanical Closet
DOAU
AHU
Water Heater
Note on M3: Tiffany Hammond: Replacement cost of units that are >15 years old.
Note on M4: Tiffany Hammond: Replacement cost of all units.

## ROOF
ROOF ASSESSMENT
DISTRICT: | 0
CAMPUS: | 0
BUILDING: | 0
| Area 1 | Area 2 | Area 3 | Area 4 | Area 5 | Area 6 | Area 7
Area ID
Approx. Sq. Ft.
Type of Roof
Reported Age | [7 empty] | Enter Reported Installation Date, not the age in years.
Slope
Condition Detail | [7 empty] | Run a spell check after completing sheet.
Visible Damage
Debris & Dirt
Fading or Chalking
Surface Degradation
Expansion Joints
Edges / Lap Joints
Flashings
Firmness, Bubbles, Fasteners
Ponding
Trees Over / On Roof
HVAC /Pipe Supports
Number of Penetrations
Approx SF of Penetrations
Feature Detail Condition
Roof Drain Pipe Condition
Debris @ RD / Scupper / Overflow
Debris in Gutters
Gutters Condition
Downspout Condition
Soffit
Fascia
Parapet
Skylights/Hatches
Interior/Supporting Surfaces
Indication of Leaks
Ceiling Condition
Perimeter Wall Condition
Rafters/Trusses/Deck Condition
Other
Assessment Results
Overall Condition Grade
Remaining Life | [7 empty] | Enter remaining life as "___ years". Include the word "years".
Immediate Action Required
Replacement Cost Factor | 0 | 0 | 0 | 0 | 0 | 0 | 0
Replacement Cost | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL REPLACEMENT COST | 0
Assessor | 0
Assessment Date | 0
Be as descriptive as possible in the Assessment Summary below. Elaborate and make recommendations on categories rated Poor/Major. Include supporting details if Immediate Action is required. If the roof is in GOOD condition, state that in the summary. (Do not leave summary blank)
Roof Assessment Summary
Drop Down Menu Values
Overall Condition | Immediate Action | Condition Ratings | Type of Roof | Slope
Good | No | Good | Standing Seam Metal | Flat
Fair | Yes | Fair | Single Ply | Low
Poor |  | Poor | BUR Gravel | Medium
|  | Inaccessible | Mod Bit | High
|  | N/A | Foam
|  | No Issues | Shingle
|  | Minor | Tin
|  | Major | Other
Inaccessible
N/A

## Renovations, Additions & Prtbls
A. RENOVATIONS
Renovation Number | Date | Construction Type | Square Footage | Usage
B. ADDITIONS
Addition Number | Date | Construction Type | Square Footage | Usage
Initial Assessor Name:
C. PORTABLE CLASSROOMS
Portable Number | Date Placed on Site | Age of Portable | Square Footage | Notes

## Security
SCHOOL SAFETY SURVEY
| YES | NO | N/A | COMMENTS
School grounds are fenced.
There is one clearly marked and designated entrance for visitors
Signs are posted for visitors to report to main office through a designated entrance.
Restricted areas are clearly marked
Shrubs and foliage are trimmed to allow for good line of sight. (3'-0"/8'- 0" rule)
Shrubs near building have been trimmed "up" to allow view of bottom of building
Bus loading and drop-off zones are clearly defined.
There is a schedule for maintenance of:
a. Outside lights
b. Locks/Hardware
c. Storage Sheds
d. Windows
e. Other exterior buildings
Parent drop-off and pick-up area is clearly defined.
There is adequate lighting around the building.
Lighting is provided at entrances and other points of possible intrusion.
The school ground is free from trash or debris.
The school is free of graffiti.
Play areas are fenced.
Playground equipment has tamper-proof fasteners
Visual surveillance of bicycle racks from main office is possible.
Visual surveillance of parking lots from main office is possible
Parking lot is lighted properly and all lights are functioning
Accessible lenses are protected by some unbreakable material
Staff and visitor parking has been designated
Outside hardware has been removed from all doors except at points of entry.
Initial Assessor Name:
a. have no broken panes;
b. locking hardware is in working order.
Basement windows are protected with grill or well cover.
Doors are locked when classrooms are vacant.
High-risk areas are protected by high security locks and an alarm system
a. Main office
b. Cafeteria
c. Computer Labs
d. Industrial Arts rooms
B SHELL
f. Nurses Office
g. Boiler Room
h. Electrical Rooms
i. Phone line access closet
Unused areas of the school can be closed off during after school activities.
There is two-way communication between the main office and:
a. Classroom
b. Duty stations
c. Re-locatable classrooms
d. Staff and faculty outside building
e. Buses
There is a central alarm system in the school. If yes, briefly describe:
The main entrance is visible from the main office.
Narratrive Executive Summary --------------------------------------------------->

## ADA
ADA SURVEY
| YES | NO | N/A | COMMENTS
There is at least 1 route from site arrival points that does not require the use of stairs.
If parking is provided for the public, there are adequate number of accessible spaces provide (1 per 25).
There is at least 1 van accessible parking space among the accessible spaces.
The slope of the accessible parking spaces and access aisles is no steeper than 1:48 in all directions.
The access aisles adjoin an accessible route.
Accessible spaces are identified with a sign that includes the International Symbol of Accessibility.
There are signs reading "van accessible" at van accessible spaces.
If the accessible route crosses a curb, there is a curb ramp.
Ramps are sloped no greater than 1:12.
The main entrance is accessible.
If the main entrance is not accessible, there is an alternative accessible entrance.
The alternative accessible entrance can be used independently and during the same hours as the main entrance.
All inaccessible entrances have signs with the International Symbol of Accessibility indicating the location of the nearest accessible entrance.
The door is equipped with hardware, including locks, that is operable with one hand and does not require tight grasping, pinching, or twisting of the wrist.
The operable parts of the door hardware are no less than 34" and no greater than 48" above the floor or ground surface.
In locker rooms, there is at least one room with a bench.
At least one toilet room is accessible (either one for each sex or one unisex).
There are signs with the International Symbol of Accessibility at inaccessible toilet rooms that give directions to accessible toilet rooms.
There is a route to the accessible toilet room(s) that does not include stairs.
The door is equipped with hardware that is operable with one hand and does not require tight grasping, pinching, or twisting of the wrist.
The operable parts of the door hardware are no less than 34" and no greater than 48" above the floor or ground surface.
The door can be opened easily (5 lbs. maximum force).
Lighting controls are operable with one hand and without tight grasping, pinching, or twisting of the wrist.
Mounted switches are no less than 34" and no greater than 48" above the floor or ground surface.
Narrative Summary --------------------------------------------------->

## IT
INFORMATION TECHNOLOGY SURVEY
| YES | NO | N/A | COMMENTS
1. Connectivity “speed “ to the Facility:
a. 10 Gbps or greater
b. 1 Gbps or greater
c. 100 Mbps or less
d. 10 Mbps or less
e. Less than 10 Mbps
2. Local area network connectivity “speed “ at the individual building level:
a. 10 Gbps or greater
b. 1 Gbps or greater
c. 100 Mbps or less
d. 10 Mbps or less
e. Less than 10 Mbps
3. Wireless Coverage:
a. Facility Wide
b. Secure?
c. Type:
i. AC
ii. N
iii. A/B/G
4. Building cabling:
a. Fiber (to the desktop)
b. CAT 6
c. CAT 5 E
d. CAT 5
5. Security:
a. Access control
Initial Assessor Name:
c. Central Communications Systems

## Harmful Substances
HARMFUL SUBSTANCES SURVEY
| YES | NO | N/A | COMMENTS
Lead
Has your facility been assessed for lead? If so when?
Is there lead in your facility?
Is lead abatement included in your future bond plans?
Asbestos
Has your facility been assessed for asbestos? If so when?
Is there asbestos in your facility?
Is asbestos abatement included in your future bond plans?
Mold
Has your facility been assessed for mold? If so when?
Is there mold in your facility?
Is mold abatement included in your future bond plans?
Water Quality
Has your facility been assessed for water quality (lead, etc)? If so when?
Is there a water quality concern in your facility?
Is water treatment included in your future bond plans?
PCBs
Has your facility been assessed for PCBs? If so when?
Are there PCBs in your facility?
Is PCB abatement included in your future bond plans?
Radon
Has your facility been assessed for Radon? If so when?
Is there Radon in your facility?
Is Radon management included in your future bond plans?

## IAQ
INDOOR AIR QUALITY SURVEY
| YES | NO | N/A | COMMENTS
Is someone designated to develop and implement an indoor air quality management plan for your school district?
Does your district have an indoor air quality management plan that includes steps for preventing and resolving indoor air quality problems?
Are school buildings inspected once or twice each year for conditions that may lead to indoor air quality problems?
Is a preventive maintenance schedule established and in operation for the heating, ventilation, and air conditioning (HVAC) system? Is the schedule in accordance with the manufacturer's recommendations or accepted practice for the HVAC system?
Does the HVAC preventive maintenance schedule include the following?: checking and/or changing air filters and belts, lubricating equipment parts, checking the motors, and confirming that all equipment is in operating order.
Is the maintenance schedule updated to show all maintenance performed on the building systems?
Does the maintenance schedule include the dates that the building systems maintenance was performed and the names of the persons or companies performing the work?
Are maintenance schedules retained for at least three years?
Are damaged or inoperable components of the HVAC system replaced or repaired as appropriate?
Are reservoirs or parts of the HVAC system with standing water checked visually for microbial growth?
Are water leaks that could promote growth of biologic agents promptly repaired?
Are damp or wet materials that could promote growth of biologic agents promptly dried, replaced, removed, or cleaned?
Are microbial contaminants removed from ductwork, humidifiers, other HVAC and building system components, and from building surfaces such as carpeting and ceiling tiles when found during regular or emergency maintenance activities or visual inspection?
Is general or local exhaust ventilation used where housekeeping and maintenance activities could reasonably be expected to result in exposure to hazardous substances above applicable exposure limits?
Does the HVAC system have CO2 monitoring capability (demand control ventilation)?
Are humidity levels maintained between 30% to 60% relative humidity?
When a contaminant is identified in the make-up air supply, is the source of the contaminant eliminated, or are the make-up inlets or exhaust air outlets relocated to avoid entry of the contaminant into the air system?
If buildings do not have mechanical ventilation, are windows, doors, vents, stacks, and other portals used for natural ventilation operating properly?

## Physical Assessment Comments (hidden)
Cell: C10
Comment: Standard spread and strip / perimeter footings; Apply rates to bldg footprint area
Cell: H10
Comment: Minor cracking observed ‐ fill and seal the cracks to prevent water intrusion
Cell: L10
Comment: Settlement observed in surrounding conditions ‐ requiring stabilization of the foundation, sub‐grade adjustment, and re‐enforcement of the foundation
Cell: C11
Comment: Pilings or other extended foundation systems that overcome non‐standard soil conditions; Apply rates to bldg footprint area
Cell: H11
Comment: Minor cracking observed ‐ fill and seal the cracks to prevent water intrusion
Cell: L11
Comment: Settlement observed in surrounding conditions ‐ requiring stabilization of the foundation, sub‐grade adjustment, and re‐enforcement of the foundation
Cell: C12
Comment: Standard ground‐set concrete slab. If slab is elevated (i.e. has a crawl space or basement), apply conditions to B1010 instead; Apply rates to bldg footprint area
Cell: J12
Comment: Separation cracks occurring requiring route and fill and patch
Cell: L12
Comment: Differential settlement occurring ‐ requires removal of section of slab, adjustment to sub‐grade, and new infill
Cell: C15
Comment: Assumed as concrete walls with water‐proofing on the exterior. Includes only the structural portion and not the wall finishes; Apply to wall surface area
Cell: H15
Comment: Inadequate below grade venting is observed ‐ cut in and add venting
Cell: J15
Comment: Wall is cracked and spalling requiring route and fill and patch and re‐finish
Cell: L15
Comment: Wall is cracked with evidence of water intrusion. Repairs to be implemented and water barrier to be applied to be applied
Cell: C18
Comment: A suspended floor including the structural members and floor construction, but not including the actual finish
Cell: J18
Comment: Deck lifting, settling, or uneven ‐ appears related to the deck itself and not the structural support below ‐ requires removal and replacement of deck
Cell: N18
Comment: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Cell: J19
Comment: Deck lifting, settling, or uneven ‐ appears related to the deck itself and not the structural support below ‐ requires removal and replacement of deck
Cell: N19
Comment: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Cell: J20
Comment: Deck lifting, settling, or uneven ‐ appears related to the deck itself and not the structural support below ‐ requires removal and replacement of deck
Cell: N20
Comment: Visible evidence of a sagging or settled structure or depression in the floor line, requiring removal and replacement
Cell: C21
Comment: The roof structure referring to the supporting structure and the deck but excluding the roofing itself
Cell: L21
Comment: Evidence of a spongy decking from water intrusion ‐ replacing the deck but not the trusses
Cell: N21
Comment: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Cell: L22
Comment: Evidence of a flexing decking from water intrusion / rust ‐ replacing the deck but not the trusses
Cell: N22
Comment: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Cell: L23
Comment: Evidence of a spongy / spalling deck from water intrusion ‐ replacing the deck but not the beams
Cell: N23
Comment: Visible evidence of a sagging structure or depression in the roof line, requiring removal and replacement
Cell: D25
Comment: Apply to wall surface area
Cell: J25
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L25
Comment: Cracks visible ‐ route and patch prior to painting
Cell: D26
Comment: Apply to wall surface area
Cell: J26
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L26
Comment: Some blocks are damaged, needing patch and repair prior to sealing or painting
Cell: N26
Comment: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Cell: D27
Comment: Apply to wall surface area
Cell: J27
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L27
Comment: A number of panels are damaged, requiring patch and repair prior to re‐painting
Cell: N27
Comment: The panels are lifting or separating or otherwise losing their integrity ‐ remove and replace
Cell: D28
Comment: Apply to wall surface area
Cell: J28
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: L28
Comment: Cracks visible ‐ route and patch prior to painting
Cell: N28
Comment: System in failure with evidence of water intrusion ‐ remove and replace
Cell: D29
Comment: Apply to wall surface area
Cell: J29
Comment: Minor repairs needed to mortar, prep, and re‐sealing
Cell: L29
Comment: Mortar missing in a majority of areas requiring complete re‐pointing and sealing
Cell: N29
Comment: Masonry visibly damaged and requiring removal and replacement
Cell: D30
Comment: Apply to glazed area
Cell: J30
Comment: The glazing is double pane but is broken or fogged and requires replacement
Cell: L30
Comment: The glazing is single pane or the sash is damaged ‐ either requires replacement of the sash and its glazing
Cell: N30
Comment: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Cell: D31
Comment: This assumes both individual aluminum windows and storefront systems; Apply to glazed area
Cell: J31
Comment: The glazing is double pane but is broken or fogged and requires replacement
Cell: L31
Comment: The glazing is single pane or the sash is damaged ‐ either requires replacement of the sash and its glazing
Cell: N31
Comment: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Cell: D32
Comment: This assumes a metal windows system clad with wood or vinyl; Apply to glazed area
Cell: J32
Comment: The glazing is double pane but is broken or fogged and requires replacement
Cell: L32
Comment: The glazing is single pane or the sash is damaged ‐ either requires replacement of the sash and its glazing
Cell: N32
Comment: The structural integrity of the frame is damaged, requiring the full replacement of the window unit
Cell: D33
Comment: Apply to glazed area
Cell: J33
Comment: Minor leaks at wall seams ‐ re‐caulk and re‐seal
Cell: L33
Comment: Window panels fogged and require replacement
Cell: N33
Comment: Settlement or displacement is evident
Cell: D34
Comment: Apply to door count
Cell: J34
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L34
Comment: Door panel and hardware are damaged and require replacement
Cell: N34
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D35
Comment: Apply to door count
Cell: J35
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L35
Comment: Door panel and hardware are damaged and require replacement
Cell: N35
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D36
Comment: Apply to door count
Cell: J36
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L36
Comment: Door panel and hardware are damaged and require replacement
Cell: N36
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: C38
Comment: Assumes the insulation, roof covering, and associated flashings, gutters, and downspouts
Cell: D38
Comment: Apply to roof area
Cell: H38
Comment: Small number of shingles lifting and/or separation in a portion of flashing
Cell: J38
Comment: Leaks in a specific area or zone related to poor detailing and or flashing
Cell: L38
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ Replace roof system OVER TOP OF EXISTING
Cell: N38
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ REMOVE AND Replace roof system
Cell: D39
Comment: Apply to roof area
Cell: H39
Comment: Minor blistering requiring isolated patches
Cell: J39
Comment: Leaks in a specific area or zone related to poor detailing and or flashing or unchecked blisters
Cell: L39
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ Replace roof system OVER TOP OF EXISTING
Cell: N39
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ REMOVE AND Replace roof system
Cell: D40
Comment: Apply to roof area
Cell: H40
Comment: Minor blistering requiring isolated patches
Cell: J40
Comment: Leaks in a specific area or zone related to poor detailing and or flashing or seam separation
Cell: L40
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ Prep and re‐coat roof system OVER TOP OF EXISTING
Cell: N40
Comment: System in complete failure with multiple leaks and multiple examples of visible breaches in system ‐ REMOVE AND Replace roof system
Cell: D41
Comment: Apply to roof area
Cell: J41
Comment: Leaks are occurring and flashing at seams or transitions has separated requiring replacement of flashing and sealant
Cell: N41
Comment: Panels have lifted or separated and water intrusion is evident. Remove and replace panels and associated flashing
Cell: D42
Comment: Apply to roof area
Cell: J42
Comment: Leaks occurring at isolated areas requiring grout removal and re‐grout at isolated tile locations
Cell: N42
Comment: Tiles are cracked, loose, or damaged and require removal and replacement
Cell: D43
Comment: Apply to roof opening area
Cell: J43
Comment: Minor leaking is occurring, requiring re‐caulk and re‐seal
Cell: N43
Comment: The panes or framing are damaged beyond repair and requires replacement
Cell: D44
Comment: Apply to roof opening area
Cell: N44
Comment: The door is non‐functional or damaged beyond repair and requires replacement
Cell: D47
Comment: Apply to wall surface area
Cell: N47
Comment: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Cell: D48
Comment: Apply to wall surface area
Cell: L48
Comment: There are some blocks that are damaged and requires a strategic removal and replacement
Cell: N48
Comment: There is evidence of settling, failure, or a compromised structure that requires removal and replacement
Cell: D49
Comment: Apply to door count
Cell: J49
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L49
Comment: Door panel and hardware are damaged and require replacement
Cell: N49
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D50
Comment: Apply to door count
Cell: J50
Comment: Door hardware is damaged or non‐functional and requires replacement
Cell: L50
Comment: Door panel and hardware are damaged and require replacement
Cell: N50
Comment: Door frame, door, and hardware are damaged and require replacement
Cell: D53
Comment: Apply to stair flights
Cell: L53
Comment: Rails not compliant with code and require removal and replacement
Cell: N53
Comment: Structural integrity of stair unit is compromised and requires its removal and replacement
Cell: D54
Comment: Apply to stair flights
Cell: H54
Comment: Rust visible ‐ prep and re‐finish
Cell: L54
Comment: Rails not compliant with code and require removal and replacement
Comment: Structural integrity of stair unit is compromised and requires its removal and replacement
Cell: D55
Comment: Apply to stair flights
Cell: L55
Comment: An isolated structural crack or separation requiring re‐enforcement in place
Cell: N55
Comment: Structural cracking and separation occurring in multiple locations ‐ remove and replace the stair unit
Cell: D56
Comment: Apply stair tread and riser area
Cell: H56
Comment: Surface feels rough and/or taking in moisture from the surface resulting in staining ‐ prep and re‐seal
Cell: N56
Comment: Severe cracking requiring removal and replacement of tread in fills
Cell: D57
Comment: Apply stair tread and riser area
Cell: N57
Comment: finish is lifting or separating and creating trip hazards ‐ remove and replace
Cell: D59
Comment: Apply to surface treated
Cell: H59
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: N59
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D60
Comment: Apply to surface treated
Cell: H60
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: J60
Comment: Surface is damaged ‐ patching of the surface is required prior to painting
Cell: N60
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D61
Comment: Apply to surface treated
Cell: H61
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: N61
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D62
Comment: Apply to surface treated
Cell: H62
Comment: Grout is damaged or deteriorated
Cell: N62
Comment: Tiles are cracked or in disrepair
Cell: D63
Comment: Apply to surface treated
Cell: N63
Comment: worn or severely stained or starting to pull up / bubble
Cell: D64
Comment: Apply to surface treated
Cell: H64
Comment: sporadic number of tiles are lifting or cracked / broken and require replacement
Cell: L64
Comment: The majority of tiles are lifting, cracking / broken and require replacement ‐ the tiles or glue are NOT asbestos
Cell: N64
Comment: The majority of tiles are lifting, cracking / broken and require replacement ‐ the tiles or glue are asbestos
Cell: D65
Comment: Apply to surface treated
Cell: N65
Comment: Severely worn or seams separating ‐ replace
Cell: D66
Comment: Apply to surface treated
Cell: H66
Comment: Surface feels rough and/or taking in moisture from the surface resulting in staining ‐ prep and re‐seal
Cell: N66
Comment: Significant cracking, but not differential ‐ requires prep and crack filling prior to re‐seal. If differential, refer to slab on grade of floor construction above
Cell: D67
Comment: Apply to surface treated
Cell: H67
Comment: Grout is damaged or deteriorated
Comment: Tiles are cracked or in disrepair
Cell: D68
Comment: Apply to surface treated
Cell: N68
Comment: Systemic blistering or severely worn traffic areas ‐ strip and replace
Cell: D69
Comment: Apply to surface treated
Cell: J69
Comment: Surface is damaged ‐ requires sanding, repair, and re‐coat / re‐stripe
Cell: N69
Comment: Wood planks are deteriorated, separating, and multiple dead spots ‐ replace floor
Cell: D70
Comment: Apply to surface treated
Cell: H70
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: J70
Comment: Surface is damaged ‐ patching of the surface is required prior to painting
Cell: N70
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D71
Comment: Apply to surface treated
Cell: H71
Comment: Stained or damaged ceiling tiles
Cell: J71
Comment: Diagonal bracing missing from grid
Cell: N71
Comment: Grid is sagging with tiles compromised ‐ requires replacement of system
Cell: D72
Comment: Apply to surface treated
Cell: H72
Comment: Stained or damaged ceiling tiles
Cell: N72
Comment: Systemic failure of finish, possible water intrusion ‐ requires removal and replacement
Cell: D73
Comment: Apply to surface treated
Cell: N73
Comment: Surface is in tact but finish is deteriorated ‐ paint
Cell: C76
Comment: Assume standard cab‐style elevator; Apply per stop
Cell: E76
Comment: Insert number of elevators * number of stories ‐ i.e. if there are 2 elevators each going 3 stories ‐ insert 6
Cell: H76
Comment: The elevator doors are damaged and require replacement
Cell: J76
Comment: Electrical components are not working
Cell: L76
Comment: Replacement of the hoist cables, guide rails, or other similar mechanical components is required
Cell: N76
Comment: Mechanical and electrical components have deteriorated requiring the replacement of the system
Cell: C77 Comment: Apply per flight
Cell: E77
Comment: Insert number of escalators * number of stories ‐ i.e. if there are 2 escalators each going 3 stories ‐ insert 6
Cell: J77
Comment: Electrical components are not working
Cell: N77
Comment: Mechanical and electrical components have deteriorated requiring the replacement of the system
Cell: C78
Comment: Assume open vertical or inclined lift; Apply per unit
Cell: E78
Comment: Insert number of lifts
Cell: J78
Comment: Electrical components are not working
Cell: N78
Comment: Mechanical and electrical components have deteriorated requiring the replacement of the system
Cell: C80
Comment: All fixtures (toilets, urinals, sinks, showers, etc.) to be lumped together here
Cell: J80
Comment: Flush valves or faucets are non‐functional and require replacement
Cell: N80
Comment: The fixture itself is broken or is not compliant with water efficiency standards
Cell: H81
Comment: The vale stems, pressure gauges, and gate valves no longer function.
Cell: J81
Comment: The insulation on the piping is in disrepair, loose, or missing.
Cell: N81
Comment: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Cell: H82
Comment: In some areas, there are back ups requiring the replacement of the broken floor or wall, clean outs, routing and cleaning the problem areas, and snaking floor drains
Cell: N82
Comment: The runs and risers are deteriorated, displaced, or have systemic leaks and requires full replacement
Cell: C83
Comment: This is for the presence of interior rain drains; note building percentage based on area of roof served ‐ excludes external downspouts
Cell: J83
Comment: The rain drain or overflow is damaged and needs replacement
Cell: N83
Comment: The integrity of the piping is compromised and is leaking inside the walls
Cell: C86
Comment: This assumes gas piping
Cell: H86
Comment: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Cell: N86
Comment: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Cell: H87
Comment: The burner is inefficient and requires refurbishment
Cell: J87
Comment: One major component needs to be replaced
Cell: L87
Comment: More than one major component needs to be replaced
Cell: N87
Comment: The system is in failure
Cell: L88
Comment: Some of the distribution fans and coils are dysfunctional.
Cell: N88
Comment: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Cell: J89
Comment: A small number of minor parts need to be repaired or replaced
Cell: L89
Comment: The burner, combustion chamber, or fan are faulty and require replacement
Cell: N89
Comment: The entire furnace requires replacement
Cell: J90
Comment: A small number of minor parts need to be repaired or replaced
Cell: L90
Comment: System operating at low efficiency; shell exhibits corrosion. Retube heat exchanger
Cell: N90
Comment: System operates at low efficiency with corrosion and leaks apparent. Replace system
Cell: L91
Comment: Some of the distribution fans and coils are dysfunctional.
Cell: N91
Comment: The majority of the distribution fans or coils are dysfunctional and the primary unit is in a state of disrepair
Cell: N92
Comment: The chiller is beyond economic repair
Cell: J93
Comment: Dampers in the system are inoperative
Cell: L93
Comment: The insulation is damaged or missing
Cell: N93
Comment: The ductwork is damaged or inadequately designed and requires replacement
Cell: H94
Comment: The valve stems, riser gate valves, and temperature probes need to be repaired or replaced.
Cell: J94
Comment: The insulation on the piping is in disrepair, loose, or missing.
Cell: N94
Comment: The risers are worn, damaged, or clogged beyond repair. Replacement includes the piping, insulation, and valves
Cell: N95
Comment: Entire unit is failing to function
Cell: J96
Comment: Internal compressor is bad and requires replacement
Cell: N96
Comment: Entire unit is failing to function
Cell: H97
Comment: In‐room valve is failing and requires replacement
Cell: N97
Comment: Entire unit is failing to function
Cell: L98
Comment: Some of the sensors or valve actuators are dysfunctional. Replace these sensors or actuators
Cell: N98
Comment: The majority of sensors or actuators are faulty, and the system software is dysfunctional OR the system is an older / obsolete pneumatic system ‐ replace
Cell: N99
Comment: One or more zones require re‐balancing
Cell: J102
Comment: Sprinkler heads are inoperable or non‐compliant and need to be replaced
Cell: N102
Comment: The piping has deteriorated or clogged or is non‐compliant and needs to be replaced, including heads
Cell: J103
Comment: The Siamese twin connection, tamper flow switches, or flow control valves are inoperable and need to be replaced
Cell: N103
Comment: The fire pump is beyond repair and needs to be replaced
Cell: C104
Comment: Assume chemical extinguishing system
Cell: J104
Comment: The back‐up tank has been discharged or lacks pressure and needs to be replaced
Cell: N104
Comment: The system is non‐functional or not compliant with the current needs and needs to be replaced
Cell: J107
Comment: Wiring has systemic problems or does not meet code and needs to be replaced
Cell: L107
Comment: Branch panels are obsolete with replacement breakers difficult to acquire and requires replacement
Comment: Main switchgear is obsolete or undersized and requires replacement, including service into building
Cell: L108
Comment: The lighting fixtures are obsolete or non‐functional and require replacement
Cell: N108
Comment: Replacement of fixtures is requiring the replacement of the wiring as well ‐ includes fixtures AND wiring
Cell: J109
Comment: There are individual devices that are not functional.
Cell: L109
Comment: The master control panel is obsolete or not functional
Cell: N109
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J110
Comment: There are individual devices that are not functional.
Cell: L110
Comment: The master control panel is obsolete or not functional
Cell: N110
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J111
Comment: There are individual devices that are not functional.
Cell: L111
Comment: The master control panel is obsolete or not functional
Cell: N111
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J112
Comment: There are individual devices that are not functional.
Cell: L112
Comment: The master control panel is obsolete or not functional
Cell: N112
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J113
Comment: There are individual devices that are not functional.
Cell: L113
Comment: The master control panel is obsolete or not functional
Cell: N113
Comment: The system is obsolete or works intermittently in multiple areas and requires a system replacement
Cell: J114
Comment: There are individual devices that are not functional or in regular alarm
Cell: L114
Comment: The master control panel is obsolete or not functional
Cell: N114
Comment: The entire system is dysfunctional and constantly in trouble mode with areas not fully covered. Remove and replace system
Cell: H115
Comment: Individual room sensors are failing and require replacement
Cell: L115
Comment: The central control panel and software need upgraded
Cell: N115
Comment: The entire system is in failure and requires replacement of sensors, wiring and central panel
Cell: H120
Comment: 2‐3 pieces of equipment require replacement
Cell: J120
Comment: Counters and sinks are not code compliant and require replacement with stainless steel and sink system
Cell: L120
Comment: Walk‐in cooler and freezer are not functional or function intermittently and require replacement
Cell: N120
Comment: Walk‐ins and kitchen design does not meet current functional requirements or has become obsolete and requires complete replacement as a full prep kitchen
Cell: H121
Comment: 2‐3 pieces of equipment require replacement
Cell: L121
Comment: Mechanical and electrical service upgrades are required to meet code and amount of program equipment
Cell: N121
Comment: Both mechanical and electrical AND equipment needs replacement to meet program criteria and code
Cell: J122
Comment: Room lacking (and needing) eye wash or fume hood
Cell: L122
Comment: Sinks are in disrepair and require replacement
Comment: Work stations need upgrades to meet current program criteria ‐ replace
Cell: J123
Comment: Storage units damaged or in disrepair
Cell: L123
Comment: Sinks are in disrepair and require replacement
Cell: N123
Comment: Work stations need upgrades to meet current program criteria ‐ replace
Cell: E124
Comment: Insert number of seats
Cell: J124
Comment: Seats damaged and need replacement OR sound OR lighting system inadequate and needs upgraded
Cell: L124
Comment: Fly rigging in disrepair and needs upgrading
Cell: N124
Comment: 2 or more stage system dysfunctional and needs upgrade / replacement to production systems
Cell: H125
Comment: An accessory is damaged or missing
Cell: J125
Comment: Accessories need to be replaced to meet ADA
Cell: L125
Comment: The stall doors are not functional or missing and need to be replaced
Cell: N125
Comment: The restrooms stall structure is failing or needs re‐configuration and needs to be replaced
Cell: D126
Comment: Note anything specific in the "Other" category at the bottom of the assessment form
Cell: C129
Comment: Assume fixed casework (counters, cabinets, shelving, etc.)
Cell: H129
Comment: The counter top or exposed surface has been damaged and can be refinished
Cell: J129
Comment: The drawers and/or doors are damaged and require replacement including hardware
Cell: L129
Comment: A combination of minor and moderate action is required, but the box is still salvageable
Cell: N129
Comment: The casework is severely damaged throughout or is obsolete for the purposes of the space and needs to be replaced
Cell: C130
Comment: Assume loose furnishings (desks, chairs, tables, etc.)
Cell: N130
Comment: The furnishings are severely worn or are inappropriate for the age of students or function of space and require replacement
Cell: C136
Comment: Paved only or needs to be paved; Apply to surface area
Cell: E136
Comment: Indicate SF of road
Cell: H136
Comment: Minor cracking exists and can be resolved with application of a slurry coat
Cell: L136
Comment: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Cell: N136
Comment: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over‐ex of sub‐grade with complete replacement. Where there is only a gravel road and a paved one is needed, this category shall be used
Cell: C137
Comment: Paved only or needs to be paved; Apply to surface area
Cell: E137
Comment: Indicate number of stalls
Cell: H137
Comment: Minor cracking exists and can be resolved with application of a slurry coat
Cell: L137
Comment: Surface is alligatoring requiring a section to be removed down to gravel base, replaced, and region slurry coated
Cell: N137
Comment: Surface is broken and shows evidence of heaving and/or settlement requiring removal of asphalt and over‐ex of sub‐grade with complete replacement. Where there is only a gravel lot and a paved one is needed, this category shall be used
Cell: C138
Comment: Concrete only or needs to be concrete; Apply to surface area
Cell: E138
Comment: Indicate square footage of walks and plazas
Cell: L138
Comment: Sections are broken with differential settlement requiring the removal of the effected panels and replacement
Cell: N138
Comment: Not only are sections of the concrete broken, but there is evidence of settlement surrounding the walk requiring removal through sub‐grade and replacement. Where there is no concrete walk, but one is needed, this category shall be used
Cell: C139
Comment: Chain‐link fencing; Apply to LF of fence
Cell: E139
Comment: Indicate length of fencing ‐ assuming 6' high chain‐link
Cell: L139
Comment: The fence fabric is damaged and needs to be replaced
Cell: N139
Comment: The fencing has lost its structural integrity and is beyond repair.
Cell: C140
Comment: Irrigation systems. Other landscape or field items should be included in "Other" category at bottom of assessment form; Apply to landscape area
Cell: E140
Comment: Indicate square footage of landscaped area served (including grass areas)
Cell: N140
Comment: Irrigation system is dysfunctional and beyond repair
Cell: D142
Comment: Assumes 4" line to building. Wells should be placed in "Other" category at bottom of form; Apply to surface area
Cell: N142
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: D143
Comment: Assumes 6" line to building. Wells and holding tanks should be placed in "Other" category at bottom of form; Apply to surface area
Cell: N143
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C144
Comment: Lines only. Septic fields, tanks, etc. should be placed in "other" category at bottom of form; Apply to surface area
Cell: N144
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C145
Comment: Assumes underground system. For surface runoff system, apply to "Other" category at bottom of form; Apply to surface area
Cell: H145
Comment: Catch basins have lost their integrity or are out of alignment. Remove catch basin, reset, and realign
Cell: J145
Comment: Storm sewer piping is dysfunctional or damaged. Remove and replace.
Cell: L145
Comment: Detention/retention has failed, but piping and catch basins are functional. Replace detention / retention system
Cell: N145
Comment: The entire underground system has failed and requires removal and replacement of all components
Cell: C146
Comment: Apply to surface area
Cell: N146
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C147
Comment: Apply to surface area
Cell: N147
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: C148
Comment: Natural gas lines; Apply to surface area
Cell: N148
Comment: A portion of the line has lost its structural integrity and requires replacement
Cell: D151
Comment: Assumes the private portion of the service lines typically underground after the meter or transformer; Apply to surface area
Cell: L151
Comment: The transformer no longer functions and is in need of replacement
Cell: N151
Comment: The service has failed and is beyond repair or is undersized requiring replacement of transformer and service lines
Cell: D152
Comment: Apply to generator quantity
Cell: H152
Comment: The generator needs to be tuned up
Cell: J152
Comment: The valves or other engine parts need to be repaired or replaced and then a tune up
Cell: L152
Comment: Generator is non‐functional or under‐sized
Cell: N152
Comment: The system (generator, tank, services lines connected lighting system) is non‐functional or under‐sized
Cell: C153
Comment: Apply to surface area
Cell: J153
Comment: The fixtures are nonfunctional and require replacement
Cell: N153
Comment: The fixtures, supports, and underground wiring need to be replaced
Cell: C154
Comment: Assumes low voltage lines underground; Apply to surface area
Cell: N154
Comment: Site cabling is inadequate or service is interrupted ‐ replace cabling
Cell: C158
Comment: For assessment professional to hand enter for specialty items and systems that do not fit into categories above